## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of DISTINCT_UNITS | Sum of EVENT_COUNT | Sum of MWLost | Sum of MWHrsLost
0020-Coal car dumpers; shakers; and unloaders | 5 | 5 | 919.64 | 3823.0196
0022-Unloading/receiving hopper (train/truck) | 25 | 25 | 487 | 2231.5499
0024-Rotary plow | 12 | 12 | 271 | 2424.9499
0028-Dust collection system | 9 | 9 | 1391 | 6277.233
0030-Coal conveyors and feeders | 240 | 243 | 40027.2 | 475136.3931
0035-Metal detector/collector (including magnetic separator) | 7 | 7 | 224.39 | 6352.5191
0040-Coal elevators | 2 | 2 | 32 | 250.0833
0050-Coal storage fires | 10 | 10 | 1564 | 151756.3161
0060-Coal crushers including motors | 33 | 33 | 3430.9 | 4986.779
0075-Storage silos/hoppers | 35 | 35 | 3274.4 | 725813.7658
0080-Stackers/reclaimers | 11 | 11 | 1259.17 | 9284.966
0084-Coal conveyor scales-storage coal pile | 12 | 12 | 1205.3 | 6575.9898
0085-Bunker feeder coal scales | 2 | 2 | 146 | 111.3999
0090-Bunker fires | 16 | 16 | 2598.29 | 221987.522
0095-Bunker flow problems | 145 | 146 | 8062.01 | 51026.852
0100-Bunker gates | 5 | 5 | 473.34 | 3255.7384
0105-Bunker structures | 4 | 4 | 26.66 | 3683.3693
0107-Screen (prior to bunkers) | 3 | 3 | 71 | 78.4333
0110-Other coal fuel supply problems up through bunkers | 81 | 81 | 14500.77 | 156136.8859
0111-Solid fuel feeder conveyors | 83 | 84 | 2957.74 | 22153.4412
0112-Solid fuel feed tanks/hoppers | 2 | 2 | 50 | 156.6667
0114-Solid fuel volumetric feeder | 2 | 2 | 15.3 | 64.3
0115-Solid fuel gravimetric feeder | 16 | 16 | 262.96 | 1499.2716
0119-Solid fuel crushers | 1 | 1 | 70.4 | 352
0121-Other solid fuel feed problems | 61 | 61 | 1842.26 | 10261.8006
0126-Coal crusher lube oil system | 1 | 1 | 10 | 3
0127-Other coal crusher dryer problems (see code 0106) | 6 | 6 | 453.66 | 2874.8518
0129-Other coal processing system problems | 47 | 50 | 4862.65 | 100841.4871
0132-Sorbent handling feeders | 1 | 1 | 37.83 | 310.206
0134-Sorbent handling crushers | 2 | 2 | 57.8 | 193
0160-Bed material tanks/hoppers | 1 | 1 | 50 | 243.3333
0163-Bed material feeders | 1 | 1 | 30 | 208.5
0170-Bed material cyclone | 1 | 1 | 39 | 180.05
0174-Other bed material handling equipment | 5 | 5 | 251.94 | 1688.1666
0200-Pulverizer exhauster fan (for indirect firing) | 30 | 30 | 1716.33 | 38474.7323
0205-Pulverizer exhauster fan drive | 14 | 14 | 996.43 | 62395.0409
0220-Pulverizer system cyclone separator | 2 | 2 | 144 | 1560
0240-Pulverized coal bin | 43 | 43 | 7188 | 37860.0814
0250-Pulverizer feeders | 1697 | 1731 | 168540.61 | 846180.0838
0253-Pulverizer feeder motor | 79 | 79 | 7021.7 | 100504.9325
0255-Pulverizer feeder coal scales | 18 | 18 | 1225.92 | 7957.2828
0256-Seal air system (air to pulverizers) | 28 | 28 | 3972.3 | 37897.2755
0257-Coal Crusher/dryer between feeder and pulverizer | 6 | 6 | 705 | 4152.5831
0260-Primary air fan | 150 | 167 | 22697.58 | 477738.1948
0262-Primary air fan lube oil system | 16 | 16 | 3535.71 | 115638.7556
0263-Primary air fan drives | 79 | 79 | 15260.28 | 370844.8819
0264-Other primary air fan problems | 69 | 69 | 15167.63 | 251221.912
0265-Primary air heater | 11 | 11 | 1879.08 | 97785.3727
0266-Primary air heater fouling | 21 | 21 | 129.8 | 11407.7865
0267-Primary air flow instrumentation | 54 | 54 | 7403.65 | 36042.4232
0270-Primary air duct and dampers | 126 | 126 | 15772.54 | 400085.4247
0280-Pulverizer fires | 131 | 133 | 17047.93 | 390651.7585
0290-Pulverizer reduced capacity due to wear | 9 | 9 | 465 | 3292.3665
0300-Pulverizer motors and drives | 136 | 140 | 12963.42 | 190839.0461
0310-Pulverizer mills | 971 | 995 | 99926.51 | 1433794.9167
0312-Pulverizer mill classifiers | 39 | 39 | 4191 | 95074.8657
0313-Pulverizer mill trunnion seals | 12 | 12 | 1419.32 | 23278.8915
0314-Pulverizer mill ball charger hopper (ball mills only) | 3 | 3 | 120 | 1052.7666
0315-Pulverizer mill coal level controls | 15 | 15 | 1099 | 16144.1331
0320-Foreign object in Pulverizers mill | 110 | 113 | 9402.34 | 63938.7525
0325-Pulverizer skidding | 17 | 17 | 1511.87 | 19168.6762
0330-Pulverizer coal leak (pulverizers only) | 132 | 134 | 11239.45 | 131419.8234
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 101 | 101 | 9203.82 | 134490.8433
0335-Pulverizer lube oil system | 157 | 157 | 15079.67 | 87425.2334
0338-Pulverizer control systems (temperature and pressure) | 108 | 108 | 11518.17 | 81801.1117
0339-Pulverizer System Puff | 9 | 9 | 1298.48 | 66126.648
0340-Other pulverizer problems | 455 | 455 | 41676.57 | 566148.1903
0341-Pulverizer deluge system | 1 | 1 | 51 | 155.55
0342-Pulverizer inert system | 9 | 9 | 1102.53 | 7507.2397
0344-Pulverizer inspection | 83 | 83 | 7473.98 | 196632.4228
0345-Pulverizer overhaul | 18 | 18 | 1205.79 | 65114.0931
0346-Pulverizer pyrite removal system | 179 | 179 | 14774.27 | 63315.1995
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 162 | 163 | 15315.17 | 263984.4092
0358-Oil burner piping and valves | 20 | 20 | 3421.4 | 20523.1573
0359-Gas burner piping and valves | 149 | 149 | 23838.84 | 331612.059
0360-Burners | 117 | 117 | 8870.24 | 636799.8641
0366-Duct burners (FBC only) | 2 | 2 | 233.12 | 6326.6919
0370-Burner instruments and controls (except light-off) | 122 | 123 | 17893.77 | 167972.4679
0380-Light-off (igniter) systems (including fuel supply) | 83 | 83 | 14670.76 | 86919.0359
0385-Igniters | 72 | 73 | 10532.04 | 88384.7688
0390-Burner wind boxes and dampers | 12 | 12 | 2523.76 | 31912.5832
0400-Burner wind box fires | 8 | 8 | 1271.4 | 29448.8331
0410-Other burner problems | 97 | 97 | 4933.71 | 33267.7262
0415-Cyclone feeders | 266 | 267 | 17020.23 | 306843.7395
0420-Cyclone crusher | 18 | 18 | 771 | 31978.0499
0425-Cyclone dampers | 17 | 17 | 1112.13 | 68315.6569
0426-Cyclone air ducts | 4 | 4 | 126.75 | 458.5333
0430-Cyclone furnace | 13 | 13 | 1292.01 | 53772.811
0435-Other cyclone problems | 273 | 434 | 13401.66 | 209640.7882
0440-Fuel oil pumps (general) | 3 | 3 | 677.3 | 1231.4498
0441-Fuel oil pumps (burner supply) | 1 | 1 | 126 | 3402
0460-Fuel oil atomizers | 8 | 8 | 1549 | 2879.2825
0470-Oil and gas fires | 9 | 9 | 1686 | 10158.7493
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 93 | 93 | 12119.75 | 104442.3731
0500-Main steam piping up to turbine stop valves | 282 | 283 | 15478.78 | 564431.2569
0510-Main steam relief/safety valves off superheater | 59 | 59 | 10268.22 | 912257.3996
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 50 | 50 | 14614.91 | 560705.5758
0530-Other main steam system problems | 113 | 116 | 13774.95 | 552778.7793
0540-Hot reheat steam piping up to turbine stop valves | 32 | 32 | 8161.39 | 1135415.4536
0541-Cold reheat steam piping up to boiler | 12 | 12 | 2351.13 | 287644.6652
0550-Reheat steam relief/safety valves | 42 | 42 | 6049.99 | 126935.7983
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 38 | 38 | 7423.85 | 52188.7578
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 22 | 22 | 3362.6 | 61918.0661
0570-Other reheat steam problems | 104 | 116 | 5728.67 | 197664.6915
0580-Desuperheater/attemperator piping | 18 | 18 | 3888.09 | 129061.8672
0590-Desuperheater/attemperator valves | 48 | 48 | 10312.44 | 355258.6377
0600-Desuperheater/attemperator spray nozzles | 20 | 20 | 654 | 6467.7165
0620-Other desuperheater/attemperator problems | 21 | 21 | 5696.2 | 81485.1576
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 2 | 2 | 364.6 | 12376.3031
0640-Startup bypass system valves | 41 | 41 | 21969.87 | 527605.7028
0650-Startup bypass tanks or flash tanks | 2 | 2 | 972 | 3489.6664
0655-Steam by-pass system instrumentation and controls | 2 | 2 | 1253 | 3516.7997
0660-Other startup bypass system problems | 5 | 5 | 1414.9 | 9050.6014
0670-Feedwater piping downstream of feedwater regulating valve | 14 | 14 | 2824 | 73984.8655
0680-Feedwater valves (not feedwater regulating valve) | 30 | 30 | 5029.34 | 130449.8517
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 8 | 8 | 1624.13 | 38213.6137
0700-Blowdown system valves A | 6 | 6 | 1273 | 6283.2998
0710-Blowdown system piping B | 7 | 7 | 2365.3 | 304311.2459
0730-Other blowdown system problems | 3 | 3 | 759.3 | 17517.5914
0740-Boiler recirculation pumps | 53 | 53 | 9546.94 | 658138.4976
0741-Boiler recirculation pumps - motors | 201 | 277 | 13433.38 | 253690.7389
0742-Boiler recirculation pumps - motors - cooling system | 10 | 10 | 1258.76 | 156068.9641
0750-Boiler recirculation piping including downcomers | 10 | 10 | 3131 | 228331.3323
0760-Boiler recirculation valves | 14 | 14 | 4196 | 74302.6987
0770-Other boiler recirculation problems | 22 | 22 | 2654 | 47776.0325
0775-Economizer piping | 25 | 25 | 5038.29 | 234609.4894
0780-Headers between tube bundles | 3 | 3 | 1287 | 1939286.5496
0790-Pipe hangers; brackets; supports (general) | 7 | 7 | 2250.7 | 202516.0343
0799-Other miscellaneous piping system problems | 29 | 29 | 5578.47 | 269659.8435
0800-Drums and drum internals (single drum only) | 51 | 51 | 15954.29 | 132073.1109
0801-HP Drum (including drum level trips not attributable to other causes) | 79 | 79 | 12697.09 | 88031.9537
0802-IP Drum (including drum level trips not attributable to other causes) | 54 | 54 | 8640.2 | 28299.4896
0803-LP Drum (including drum level trips not attributable to other causes) | 25 | 25 | 3553.56 | 8385.6551
0810-Boiler supports and structures (use code 1320 for tube supports) | 1 | 1 | 18 | 288.3
0820-Casing | 31 | 31 | 7151.99 | 1124316.5409
0830-Doors | 27 | 27 | 5249.48 | 120570.5291
0840-Refractory and insulation | 11 | 11 | 1105.6 | 100987.8929
0845-Windbox expansion joints | 2 | 2 | 92 | 813.1667
0847-Other expansion joints | 14 | 14 | 2294.6 | 208700.0841
0850-Other internal or structural problems | 20 | 20 | 563.07 | 47391.4722
0855-Drum relief/safety valves (Single drum only) | 30 | 31 | 3955.11 | 52832.9712
0858-LP Drum relief/safety valves | 2 | 2 | 189.4 | 91.5433
0859-Tube external fins/membranes A | 13 | 13 | 3447.6 | 507624.9757
0860-Soot blowers - air (see code 3844 for air delivery system) | 11 | 11 | 1451.5 | 42123.3331
0870-Soot blowers - steam | 14 | 14 | 3037.32 | 23192.2026
0872-Soot blowers - water | 7 | 7 | 1586.3 | 27702.4665
0876-Soot blower controls | 37 | 37 | 4201.3 | 42172.1273
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 127 | 128 | 12022.47 | 175119.2378
0885-Fly ash Removal System - wet transport | 2 | 2 | 425 | 3667.4165
0890-Bottom ash systems (wet or dry) | 151 | 151 | 18623.9 | 538019.9462
0891-Bottom ash hoppers (including gates) | 21 | 21 | 3747.06 | 218035.0477
0892-Bottom ash clinker grinders | 21 | 21 | 4215.5 | 110764.6608
0893-Bottom ash water pumps and motors | 1 | 1 | 336 | 453.6
0894-Bottom ash piping and valves | 23 | 23 | 3398.27 | 30475.8749
0895-Ashpit trouble | 5 | 5 | 1307 | 40367.9162
0896-Bottom ash dewatering bin system; instruments and controls | 3 | 3 | 293.3 | 1939.1166
0897-Bottom ash rotary (drag chain type) conveyor and motor | 84 | 84 | 18250.54 | 482390.7052
0898-Bottom ash pyrite hopper (pulverizer reject) system | 3 | 3 | 580 | 2621.9999
0899-Bottom ash controls and instrumentation | 4 | 4 | 489 | 1895.7998
0900-Slag-tap (cyclone furnace) | 28 | 28 | 2506.8 | 158253.4794
0910-Slag-tap (other than cyclone furnace) | 2 | 2 | 243 | 45866.1498
0920-Other slag and ash removal problems A | 226 | 228 | 23913.7 | 253665.0501
0930-Bed material coolers | 19 | 19 | 2189.52 | 107268.9926
0931-Bed material transport piping/valves | 4 | 4 | 347.8 | 2643.4099
0933-Bed material fans/blowers | 2 | 2 | 49.83 | 1587.96
0935-Bed material disposal conditioner | 1 | 1 | 117.09 | 1287.99
0950-Other bed material system problems | 21 | 21 | 3791.6 | 74883.037
0973-Flue gas-solids separator refractory | 1 | 1 | 43 | 108.9333
0989-Other bed solids recirculation problems | 34 | 34 | 2175.72 | 63517.2424
0991-Tube leaks | 7 | 7 | 579.17 | 55826.7272
0999-Other heat exchanger problems | 1 | 1 | 140 | 1283.3332
1000-Waterwall (Furnace wall) | 708 | 709 | 230272.9 | 18252501.1524
1003-Steam generating tubes between steam drum and mud drum | 20 | 20 | 5276.4 | 296463.162
1005-Generating tubes | 17 | 17 | 2730 | 195124.5491
1010-Cyclone furnace (in cyclone area only) | 26 | 26 | 5229.29 | 371120.4546
1020-Convection pass wall (water tubes only) | 27 | 27 | 6748.93 | 633481.4829
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 18 | 18 | 5933.65 | 649298.6817
1035-Platen superheater | 58 | 58 | 24351.86 | 2506215.9917
1040-First superheater | 163 | 163 | 49828.98 | 3696339.485
1050-Second superheater | 190 | 191 | 59111.99 | 4701829.5103
1060-First reheater | 133 | 133 | 55474.95 | 5983014.0314
1070-Second reheater | 29 | 29 | 12962.5 | 957958.3799
1075-External reheater link tubing | 2 | 2 | 601 | 25688.6332
1080-Economizer | 161 | 162 | 35639.06 | 2657132.2236
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 2 | 2 | 565 | 42010.9163
1090-Other boiler tube leaks | 168 | 168 | 49429.62 | 3975575.8946
1100-Waterwall (Furnace wall) | 82 | 87 | 10578.5 | 327950.2549
1103-Steam generating tubes between steam drum and mud drum | 2 | 2 | 73.58 | 2544.0826
1105-Generating tubes | 6 | 6 | 58.6 | 33648.49
1110-Cyclone furnace (in cyclone area only) | 17 | 17 | 1065.53 | 17971.6719
1120-Convection pass wall | 2 | 2 | 181 | 25644.9999
1140-First superheater | 45 | 45 | 4326.97 | 335345.5328
1150-Second superheater | 129 | 129 | 10899.54 | 330167.1758
1160-First reheater | 51 | 51 | 3677 | 221266.5653
1170-Second reheater | 33 | 35 | 1170.25 | 42148.2705
1180-Economizer | 150 | 151 | 14429.83 | 726785.9389
1190-Other tube slagging or fouling | 110 | 110 | 10703.27 | 258185.1112
1191-Bed agglomeration (FBC only) | 7 | 7 | 246.4 | 12898.4533
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 15 | 15 | 3295 | 76726.2495
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 14 | 14 | 1467 | 47784.0495
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 4 | 4 | 751 | 49940.9662
1330-Slag fall damage | 2 | 2 | 1149.1 | 87654.2181
1350-Other miscellaneous boiler tube problems | 142 | 206 | 16588.1 | 2174006.2501
1360-Boiler drains system | 30 | 30 | 2529.6 | 107247.5491
1400-Forced draft fans | 221 | 232 | 25758.19 | 1384263.8242
1401-Forced draft fan dampers | 44 | 44 | 9058.25 | 85655.5634
1407-Forced draft fan lubrication system | 24 | 24 | 7809.8 | 131864.861
1410-Forced draft fan motors | 132 | 133 | 20029.88 | 1424039.1069
1411-Forced draft fan motors - variable speed | 10 | 10 | 2651 | 20296.6992
1412-Forced draft fan drives (other than motor) | 69 | 70 | 12756.55 | 152010.4415
1413-Forced draft fan couplings | 5 | 5 | 1625.25 | 37230.1992
1415-Forced draft fan controls | 56 | 56 | 12580.96 | 115994.3101
1420-Other forced draft fan problems | 81 | 81 | 12583.44 | 308484.2036
1421-Secondary air fans/blowers | 16 | 16 | 1449.6 | 13098.4886
1422-Secondary air fan/blower motors - single speed | 3 | 3 | 403 | 2843.1832
1424-Secondary air fan/blower controls | 6 | 6 | 700.27 | 1759.7389
1430-Air supply ducts from FD fan | 12 | 12 | 2461.18 | 520868.7687
1431-Air supply dampers from FD fan | 12 | 12 | 1940.65 | 19043.0011
1432-Air supply duct expansion joints | 15 | 15 | 3186.1 | 265445.3519
1440-Air supply dampers | 21 | 21 | 4193.9 | 65722.5785
1450-Other air supply problems | 81 | 85 | 10579.86 | 961654.055
1451-Fluidized Air Fan | 1 | 1 | 67 | 2207.65
1455-Induced draft fans | 1227 | 1239 | 85571.8 | 4102331.0115
1456-Induced draft fan dampers | 162 | 162 | 8565.03 | 238988.4283
1457-Induced draft fan lubrication systems | 69 | 69 | 19400.92 | 1512673.2773
1460-Induced draft fan fouling | 10 | 10 | 1505.72 | 58559.7653
1470-Induced draft fan motors and drives | 192 | 195 | 25715.65 | 1240167.7643
1471-Induced draft fan motors - variable speed | 101 | 101 | 18669.03 | 503204.7835
1472-Inducted draft fan coupling | 11 | 11 | 1340.68 | 43027.2854
1475-Induced draft fan controls | 181 | 182 | 32619.69 | 355742.2788
1476-Induced draft fan speed changer | 11 | 11 | 2427.47 | 28056.3092
1480-Other induced draft fan problems | 740 | 781 | 48030.08 | 1111514.6871
1487-Air heater (tubular) | 13 | 13 | 1022.36 | 61428.2837
1488-Air heater (regenerative) | 162 | 162 | 34158.97 | 1746369.4315
1489-Air heater (heat pipe; plate-type) | 12 | 12 | 1833.9 | 119384.7042
1492-Air heater fouling (tubular) | 10 | 10 | 489.2 | 21877.9531
1493-Air heater fouling (regenerative) | 244 | 252 | 13485.51 | 457897.4496
1495-Other air heater fouling (heat pipe; plate-type) | 23 | 23 | 2692.9 | 110917.5912
1500-Air heater soot blowers | 5 | 5 | 975 | 106317.8333
1510-Flue gas ducts (except recirculation) | 83 | 84 | 7585.55 | 466310.3144
1512-Flue gas expansion joints | 51 | 51 | 5546.3 | 355224.543
1520-Flue gas dampers (except recirculation) | 13 | 13 | 2201.9 | 78684.0877
1530-Other flue gas problems | 78 | 90 | 3983.11 | 1269027.1468
1535-Flue gas recirculating fan | 8 | 8 | 1418.7 | 458081.9326
1536-Flue gas recirculating fan dampers | 5 | 5 | 1113 | 9618.7495
1550-Flue gas recirculation fan motors | 4 | 4 | 455 | 11415.1666
1555-Flue gas recirculation fan controls | 6 | 6 | 3846.5 | 585499.1068
1560-Other flue gas recirculation fan problems | 8 | 8 | 480 | 67729.1333
1570-Flue gas recirculation ducts | 1 | 1 | 150 | 37197.4999
1572-Flue gas recirculation duct expansion joints | 2 | 2 | 437 | 36837.9166
1580-Flue gas recirculation dampers | 1 | 1 | 28 | 19.6
1591-Stack damper and linkage | 16 | 16 | 2551 | 36303.8325
1599-Other miscellaneous boiler air and gas system problems | 156 | 156 | 17500.2 | 350229.7951
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 242 | 242 | 55602.26 | 954486.4287
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 213 | 225 | 24522.15 | 597705.5598
1720-Desuperheater/attemperator controls | 44 | 44 | 6127.52 | 93452.5124
1730-Boiler explosion or implosion | 5 | 5 | 1048.75 | 88247.7912
1740-Boiler drum gage glasses/level indicator | 74 | 74 | 16547.65 | 85547.5634
1750-Burner management system | 190 | 191 | 43035.37 | 376687.7857
1760-Feedwater instrumentation (not local controls) | 16 | 16 | 4591.65 | 32344.0039
1761-Combustion /Steam condition instrumentation (not local controls) | 30 | 30 | 7069.2 | 104831.8614
1762-Desuperheater/attemperator instrumentation (not local controls) | 8 | 8 | 1782.7 | 8642.206
1799-Other boiler instrumentation and control problems | 255 | 255 | 62129.75 | 964856.4116
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 9 | 9 | 600.58 | 61874.6333
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 13 | 13 | 1602.18 | 42107.1084
1810-Other boiler inspections | 1 | 1 | 78 | 195546
1811-Boiler Inspections - problem identification/investigative | 4 | 4 | 788.77 | 6830.5561
1812-Boiler Inspections - scheduled or routine | 24 | 24 | 614.83 | 239051.7647
1820-Chemical cleaning/steam blows | 2 | 2 | 380 | 47987.6665
1850-Boiler water condition (not feedwater water quality) | 401 | 401 | 58791.62 | 990371.7543
1900-Improper balance between tube sections not due to fouling or plugging | 17 | 17 | 684 | 6393.2497
1910-Inadequate air not due to equipment problems | 44 | 44 | 624.98 | 51052.7483
1980-Boiler safety valve test | 12 | 12 | 1264.8 | 6352.1131
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 44 | 44 | 6815.66 | 136153.1349
1999-Boiler; miscellaneous | 392 | 395 | 28279.55 | 976884.2854
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 4 | 4 | 570.11 | 41244.2781
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 15 | 15 | 1303.33 | 17956.6416
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 5 | 5 | 218.72 | 7573.4844
2030-Fuel limits - peaking factors | 1 | 1 | 10 | 1033.8333
2035-Core xenon restrictions | 1 | 1 | 36.17 | 595.5993
2070-Normal refueling | 62 | 62 | 28361.1 | 590527.1157
2071-Refueling equipment problems | 1 | 1 | 1158 | 3782.7992
2112-Control rod hydraulic drives | 1 | 1 | 47.7 | 30.21
2120-Control rod scram mechanisms | 1 | 1 | 28.75 | 172.5
2140-Control rod drive cooling | 1 | 1 | 29 | 29
2150-Control rod instrumentation | 2 | 2 | 22 | 20.5333
2151-Control rod drive controls | 2 | 2 | 437 | 5725.8832
2152-Control rod drive power supplies | 3 | 3 | 1847.54 | 151640.3661
2155-Control rod testing | 3 | 3 | 450 | 5538.1667
2160-Other control rod drive problems | 1 | 1 | 155 | 4562.1666
2171-Reactor vessel nozzles | 2 | 2 | 1707 | 211862.5824
2174-Core support | 2 | 2 | 2200.2 | 2928948.9826
2176-Control rod guides (not in fuel) | 1 | 1 | 928 | 229432.533
2200-Reactor coolant/recirculating pumps | 11 | 11 | 8951.11 | 509593.5616
2210-Reactor coolant/recirculating pump motors | 20 | 20 | 12361.03 | 394352.976
2220-Reactor coolant/recirculating pump MG sets | 6 | 6 | 1291.24 | 89544.4422
2270-Power operated relief and safety/relief valves | 4 | 4 | 2203 | 229440.8162
2300-Recirculation loop flow control valves | 1 | 1 | 93.6 | 1798.6799
2350-BWR feedwater controls | 1 | 1 | 20 | 720
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 6 | 6 | 3266.6 | 149238.1546
2380-Reactor control system/integrated control system problems | 3 | 3 | 1237.9 | 7303.205
2390-Other reactor coolant system instruments and controls | 2 | 2 | 1206 | 190461.0667
2420-Steam generator moisture separators and dryers | 1 | 1 | 98.7 | 120.0849
2421-Steam generator feedwater nozzles | 1 | 1 | 10.7 | 1284
2440-Steam generator chemistry (excluding feedwater chemistry) | 2 | 2 | 47.01 | 433.177
2460-Blowdown system valves B | 10 | 10 | 2129.85 | 62640.1333
2480-Other blowdown | 17 | 17 | 269.73 | 130855.2423
2500-Steam piping (up to turbine stop valves and bypass valves) | 1 | 1 | 112.6 | 10653.8366
2510-Main steam isolation valves (BWR and PWR) | 4 | 4 | 2468 | 206475.6828
2540-Other steam valves | 22 | 22 | 468.04 | 189639.8433
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 1 | 1 | 0.6 | 7.51
2560-Steam generator controls | 2 | 2 | 1244 | 137200.2661
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 1 | 1 | 12 | 77
2603-High pressure piping | 3 | 3 | 1956.73 | 163436.2634
2604-High pressure valves | 1 | 1 | 981 | 319936.7997
2628-Residual heat removal/decay heat removal system | 2 | 2 | 2807 | 3887054.5329
2650-Emergency diesel generators (including actuating systems) | 2 | 2 | 1990 | 702930.2657
2660-Safeguard buses and associated equipment (transformers; breakers; etc.) | 2 | 2 | 2128 | 820292.5826
2720-Containment isolation valves and dampers | 1 | 1 | 121 | 369.05
2770-Containment cooling system - normal | 5 | 6 | 1731 | 118279.6664
2816-Valves and piping | 2 | 2 | 963 | 34272.416
2823-Nuclear closed cooling heat exchanger | 1 | 1 | 1017 | 81546.4497
2829-Other closed cooling water system problems B | 1 | 1 | 1117.24 | 135614.315
2831-Nuclear service water piping | 29 | 29 | 14220.6 | 290404.4112
2870-Radioactive liquid waste system problems | 1 | 1 | 11.01 | 264.24
2880-Radioactive gas and waste system problems | 1 | 1 | 36.19 | 546.469
2999-Other miscellaneous nuclear reactor problems | 2 | 2 | 832.6 | 19966.398
3110-Condenser tube leaks | 232 | 233 | 58560.53 | 2591027.4505
3111-Condenser tube fouling shell side | 5 | 5 | 890.3 | 4045.4481
3112-Condenser tube fouling tube side | 380 | 442 | 19879.27 | 706246.6213
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 244 | 270 | 33826.23 | 198254.542
3114-Air-cooled condenser tubes | 7 | 7 | 1274.3 | 4380.2263
3115-Air-cooled condenser pumps | 4 | 4 | 528.73 | 4173.2683
3116-Air-cooled condenser fans | 12 | 12 | 685.81 | 15919.0168
3117-Air-cooled condenser fan motors | 5 | 5 | 522.13 | 16757.3779
3118-Other Air-cooled condenser problems | 55 | 55 | 3124.5 | 16942.1857
3119-Other condenser tube casing or shell and internal problems | 12 | 12 | 4342.48 | 238769.4398
3121-Expansion joint | 9 | 9 | 2057.28 | 161239.609
3122-Gaskets and seals | 10 | 10 | 2371.51 | 139905.0925
3123-Hot well | 7 | 7 | 1172.6 | 8982.1764
3124-Tube sheet fouling | 24 | 24 | 513.82 | 4660.0732
3129-Other condenser casing or shell and internal problems | 12 | 12 | 1971.9 | 98734.9245
3130-Air ejectors | 19 | 19 | 2879.34 | 44496.991
3131-Air ejector piping and valves | 14 | 14 | 1902.89 | 6283.3369
3132-Inter and after condensers | 8 | 8 | 649 | 2865.0664
3133-Vacuum pumps | 43 | 43 | 7369.1 | 86005.6247
3134-Vacuum pump piping and valves | 19 | 19 | 4845.83 | 42620.333
3135-Vacuum pump motor and auxiliaries | 4 | 4 | 1780 | 41266.3333
3139-Other air extraction system problems - general | 6 | 6 | 511.83 | 1249.8588
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 352 | 353 | 38274.08 | 598180.2178
3150-Hot well level controls | 12 | 12 | 3238.2 | 25639.496
3151-Vacuum pump and air ejector controls | 5 | 5 | 773.83 | 12677.0042
3152-Air-cooled condenser controls | 5 | 5 | 404.19 | 1157.6879
3159-Other condensing system controls and instruments | 26 | 26 | 3826.58 | 108452.1124
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 4 | 4 | 868 | 87518.7498
3186-Auxiliary Condenser and Associated Equipment | 8 | 8 | 1435.45 | 5422.6999
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 29 | 29 | 4853.1 | 140721.6264
3199-Other miscellaneous condensing system problems | 54 | 54 | 3495.25 | 63892.5059
3210-Circulating water pumps | 208 | 222 | 28281.34 | 2035973.7285
3211-Circulating water pump motors | 134 | 135 | 19506.32 | 1110394.7336
3220-Circulating water piping | 73 | 73 | 9520.9 | 825064.3679
3221-Circulating water piping fouling | 14 | 14 | 1866 | 97897.733
3230-Circulating water valves | 40 | 40 | 7569.16 | 70389.3664
3231-Waterbox | 5 | 5 | 1009 | 137743.383
3232-Condenser tube cleaning system including debris filter | 56 | 58 | 3989.42 | 18453.6716
3233-Circulating water priming system | 2 | 2 | 362 | 1295.25
3235-Cooling tower booster pump | 2 | 2 | 810 | 10894.5
3238-Cooling tower fan motors | 14 | 14 | 1968.5 | 60698.1746
3239-Cooling tower fan motors - variable speed | 1 | 1 | 358 | 680.2
3240-Cooling tower fans | 56 | 56 | 4384.88 | 83144.3807
3241-Cooling tower efficiency below design | 113 | 117 | 2907.4 | 32254.3192
3242-Cooling tower fill damage | 3 | 3 | 540 | 102783.8333
3243-Cooling tower icing | 3 | 3 | 5 | 2.5
3245-Other cooling tower problems | 39 | 39 | 6314.83 | 257545.8449
3246-Cooling tower fouling | 9 | 9 | 924.8 | 8799.7219
3247-Cooling tower instrumentation | 15 | 15 | 2679.1 | 4028.7793
3250-Circulating water system instruments and controls | 31 | 31 | 3896.6 | 67245.1622
3260-Traveling screens | 41 | 47 | 7032.57 | 423927.8362
3261-Traveling screen fouling | 26 | 28 | 2878 | 35237.9297
3269-Circulating water biological conditions (ie; zebra mussels) | 4 | 4 | 159 | 440.1666
3270-Intake system problems other than traveling screens | 30 | 30 | 4625.8 | 47371.1254
3271-Intake grating fouling | 12 | 12 | 763.83 | 14289.9765
3272-Circulating water screenwash system | 1 | 1 | 250.4 | 4398.6932
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 53 | 53 | 9344.56 | 98094.3492
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 20 | 20 | 6574 | 175013.2811
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 129 | 130 | 5845.11 | 130106.2912
3281-Circulating water tempering system | 21 | 21 | 607 | 2921.3332
3282-Circulating water cooling ponds | 1 | 1 | 64 | 512
3285-Circulating water chemistry | 43 | 43 | 1680.1 | 11629.1396
3290-Waste water (zero discharge) tanks; pumps and motors | 1 | 1 | 310 | 2526.5
3291-Waste water (zero discharge) system fouling | 3 | 3 | 596 | 14650.3164
3295-Other Waste water (zero discharge) problems | 2 | 2 | 101 | 7292.2
3299-Other circulating water system problems | 60 | 60 | 4705.88 | 32455.8843
3300-Condensate water pre-treatment | 5 | 5 | 872 | 103535.933
3310-Condensate/hotwell pumps | 144 | 144 | 22744.37 | 656643.2475
3311-Condensate/hotwell pump motor | 43 | 43 | 5289.23 | 192055.4819
3312-Condensate booster pump | 27 | 27 | 5457.28 | 215973.2812
3313-Condensate booster pump motor | 6 | 6 | 599.5 | 9992.9331
3314-Condensate booster pump motor - variable speed | 5 | 5 | 501.7 | 63435.6616
3320-Condensate piping | 23 | 23 | 6515.4 | 451414.989
3330-Condensate valves | 36 | 36 | 7822.17 | 86024.9351
3339-LP heater head leaks | 1 | 1 | 10 | 54
3340-LP heater tube leaks | 15 | 15 | 2699.06 | 96204.0342
3341-Other LP heater - general | 22 | 22 | 3744.6 | 141671.4032
3342-IP heater tube leaks | 14 | 14 | 1831.15 | 149197.2444
3343-Other IP heater - general | 7 | 7 | 357.9 | 19306.9632
3344-Deaerator (including level control) | 67 | 67 | 13890.38 | 727378.073
3350-Condensate polishing and filtering systems | 45 | 45 | 10166.64 | 137064.7609
3351-Chemical addition systems | 6 | 6 | 1207.93 | 9784.8206
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 192 | 195 | 28089.5 | 307979.5559
3360-Condensate makeup and return (including storage tanks) | 17 | 17 | 2441.33 | 22746.4464
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 33 | 33 | 5761.05 | 17197.919
3380-Condensate coolers | 4 | 4 | 476.2 | 11132.8484
3399-Other miscellaneous condensate system problems | 17 | 17 | 2218.9 | 24955.0851
3401-Startup feedwater pump | 18 | 18 | 5811.68 | 136788.7479
3402-Startup feedwater pump drives - all types | 1 | 1 | 690 | 1563.9995
3407-Feedwater pump suction screens | 11 | 11 | 3202 | 28360.6652
3408-Feedwater pump drive - local controls | 39 | 39 | 9825.6 | 114632.2852
3409-Feedwater pump drive motor - variable speed | 4 | 4 | 221.08 | 6160.0913
3410-Feedwater pump | 499 | 499 | 91820.68 | 3371296.4483
3411-Feedwater pump drive - motor | 116 | 116 | 15278.77 | 1432890.4479
3412-Feedwater pump drive - steam turbine | 147 | 147 | 42937.01 | 3095582.3899
3413-Feedwater pump coupling and drive shaft | 28 | 28 | 8339.1 | 406690.4881
3414-Feedwater pump local controls | 67 | 67 | 20239.25 | 226696.3582
3415-Feedwater pump/drive lube oil system | 133 | 133 | 28462.26 | 513469.1632
3416-Other feedwater pump problems | 147 | 147 | 30701.51 | 623442.3467
3417-Feedwater pump drive - main shaft | 4 | 4 | 1195.79 | 61112.0609
3418-Feedwater pump drive - other | 16 | 16 | 3041.75 | 73212.2908
3419-Feedwater pump drive - gear | 4 | 4 | 1102.9 | 37091.1299
3420-Feedwater piping and supports | 42 | 42 | 11221.03 | 320193.8685
3430-Feedwater regulating (boiler level control) valve | 130 | 130 | 24231.22 | 548724.8639
3431-Other feedwater valves | 164 | 164 | 36384.71 | 1321601.8436
3439-HP heater head leaks | 22 | 22 | 3267.34 | 263920.2942
3440-High pressure heater tube leaks | 210 | 220 | 13009.43 | 1455982.9932
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 83 | 83 | 8598.95 | 405782.471
3452-Feedwater Booster Pump Drive - Local Controls | 1 | 1 | 560 | 14672
3454-Feedwater Booster Pump | 27 | 27 | 5277.17 | 454904.4462
3455-Feedwater Booster Pump Drive - Motor | 9 | 9 | 1763.1 | 93552.5212
3457-Feedwater Booster Pump Coupling and Drive Shaft | 1 | 1 | 300 | 2079.9999
3458-Feedwater Booster Pump Local Controls | 2 | 2 | 811 | 10754.0996
3459-Feedwater Booster Pump/Drive Lube Oil System | 4 | 4 | 369 | 11156.0166
3460-Other Feedwater Booster Pump Problems | 13 | 13 | 2868.93 | 75046.8703
3499-Other feedwater system problems | 210 | 210 | 27088.61 | 675571.2946
3501-Heater drain pumps | 32 | 32 | 3286.8 | 63265.5357
3502-Heater level control | 41 | 41 | 5229.76 | 139756.121
3503-Heater drain piping | 18 | 18 | 2606.17 | 107825.0236
3504-Heater drain valves | 43 | 43 | 3698.43 | 149283.0706
3505-Heater drain pump drive | 13 | 13 | 448 | 43981.4732
3509-Other heater drain system problems | 14 | 14 | 2686.82 | 167518.3463
3520-HP Extraction steam piping | 7 | 7 | 1535.74 | 87591.1481
3521-HP Extraction steam valves | 34 | 34 | 4946.36 | 97893.9087
3522-HP Extraction steam instruments and controls | 14 | 14 | 2356.39 | 21519.746
3529-Other HP extraction steam system problems | 8 | 8 | 1826.1 | 31231.8493
3530-IP Extraction steam piping | 7 | 7 | 998 | 15333.633
3531-IP Extraction steam valves | 8 | 8 | 1802.27 | 42702.8199
3532-IP Extraction steam instruments and controls | 7 | 7 | 901.84 | 23404.7716
3540-LP Extraction steam piping | 3 | 3 | 1180.7 | 151458.3981
3541-LP Extraction steam valves | 7 | 7 | 866 | 32372.3998
3542-LP Extraction steam instruments and controls | 3 | 3 | 210.5 | 3907.02
3600-Switchyard transformers and associated cooling systems - external | 26 | 26 | 2622.71 | 289927.8404
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 3 | 3 | 230 | 27912.9332
3610-Switchyard circuit breakers - (not outside management control) | 108 | 108 | 13236.94 | 398893.0089
3611-Switchyard circuit breakers - external | 167 | 167 | 23270 | 553019.2467
3612-Switchyard system protection devices - external | 90 | 90 | 10359.88 | 325390.8603
3613-Switchyard system protection devices - (not outside management control) | 40 | 40 | 5984.34 | 159368.292
3618-Other switchyard equipment ? (not outside management control) | 19 | 19 | 712.99 | 14064.349
3619-Other switchyard equipment - external | 191 | 191 | 21602.04 | 946013.6504
3620-Main transformer | 385 | 386 | 56829.41 | 11407103.9628
3621-Unit auxiliaries transformer | 117 | 118 | 23393.45 | 1751143.5133
3622-Station service startup transformer | 34 | 34 | 9908.14 | 676875.7438
3623-Auxiliary generators | 3 | 3 | 497.9 | 10053.1765
3624-Generator Voltage Supply System | 17 | 17 | 4221.99 | 258835.838
3629-Other switchyard or high voltage system problems - external | 128 | 128 | 14408.16 | 350986.8928
3630-480-volt transformers | 23 | 23 | 4955.98 | 310468.7656
3631-480-volt circuit breakers | 103 | 103 | 15696.46 | 119929.229
3632-480-volt conductors and buses | 14 | 14 | 3530.66 | 157553.731
3634-480-volt protection devices | 26 | 26 | 5343.05 | 41048.7133
3639-Other 480-volt problems | 23 | 23 | 3898.72 | 66596.8788
3640-AC instrument power transformers | 12 | 12 | 4076.07 | 592971.3279
3641-AC Circuit breakers | 61 | 61 | 5392.24 | 137733.6511
3642-AC Conductors and buses | 59 | 60 | 16173.48 | 1159335.3329
3643-AC Inverters | 26 | 26 | 6578.9 | 126419.8924
3644-AC Protection devices | 157 | 157 | 18853.83 | 1098376.2312
3649-Other AC instrument power problems | 29 | 30 | 4390.88 | 218342.0527
3650-DC instrument power battery chargers | 27 | 27 | 1843.1 | 95885.3694
3651-DC circuit breakers | 11 | 11 | 1657.4 | 8744.5258
3652-DC conductors and buses | 2 | 2 | 152.2 | 13436.8766
3653-DC protection devices | 16 | 16 | 2336.31 | 32021.155
3659-Other DC power problems | 52 | 52 | 7805.94 | 129696.0868
3660-4160-volt transformers | 7 | 7 | 1394 | 168426.1661
3661-4160-volt circuit breakers | 103 | 103 | 21469.46 | 657986.2261
3662-4160-volt conductors and buses | 48 | 48 | 12105.6 | 1294338.0689
3663-4160-volt insulators | 1 | 1 | 216.7 | 4467.6315
3664-4160-volt protection devices | 36 | 36 | 8980.85 | 102277.9929
3669-Other 4160-volt problems | 13 | 13 | 3145.31 | 26454.8835
3670-12kV transformers | 26 | 26 | 4151.17 | 326184.1121
3671-12kV circuit breakers | 45 | 45 | 4916.44 | 505188.543
3672-12kV conductors and buses | 31 | 31 | 3378.87 | 391619.9765
3673-12kV insulators | 3 | 3 | 134.19 | 4307.394
3674-12kV protection devices | 18 | 18 | 1900.19 | 218588.5198
3679-Other 12kV problems | 11 | 11 | 1376.78 | 166256.987
3680-Other voltage system transformers | 12 | 12 | 1438.36 | 249541.9078
3681-Other voltage system breakers | 62 | 62 | 9414.44 | 168298.8435
3682-Other voltage system conductors and buses | 35 | 35 | 5998.97 | 285057.3267
3683-Other voltage system insulators | 9 | 9 | 842.02 | 60734.4467
3684-Other voltage system protection devices | 86 | 86 | 7218.2 | 301524.5746
3689-Other Other voltage system problems | 35 | 35 | 3695.92 | 70987.547
3690-Station Service Power Distribution System; General | 58 | 58 | 6532.1 | 500261.8071
3700-Power Station switchyard (non generating unit equipment) | 38 | 38 | 5051.81 | 181745.2501
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 119 | 119 | 13010.85 | 1374779.9251
3720-Transmission equipment at the 1st substation) | 51 | 53 | 8399.35 | 118043.9237
3730-Transmission equipment beyond the 1st substation | 91 | 91 | 8527.1 | 228554.4376
3800-Open cooling water pumps and motors | 8 | 8 | 1044.15 | 51115.6646
3801-Open cooling water piping | 5 | 5 | 1094 | 51456.5497
3803-Open cooling water heat exchangers | 5 | 5 | 364 | 6052.3666
3806-Open cooling water strainer | 1 | 1 | 393 | 3052.2997
3809-Other open cooling water problems | 2 | 2 | 385 | 8561.6664
3810-Service water pumps and motors | 22 | 22 | 1563.26 | 40239.0759
3811-Service water piping | 16 | 16 | 1963.4 | 88389.3197
3812-Service water valves | 14 | 14 | 601.46 | 10323.6062
3814-Service water system fouling | 8 | 8 | 2279.4 | 38705.1723
3819-Other service water problems A | 37 | 37 | 2156.17 | 32613.0984
3820-Closed cooling water pumps | 16 | 16 | 2239.33 | 19815.7276
3821-Closed cooling water piping | 19 | 19 | 4200 | 521643.923
3822-Closed cooling water valves | 7 | 7 | 1490 | 6831.5994
3823-Closed cooling water heat exchangers | 29 | 29 | 3097.8 | 65126.6989
3824-Closed cooling water system fouling | 2 | 2 | 124.3 | 1689.8799
3825-Closed cooling water instrumentation | 1 | 1 | 69 | 248.4
3826-Closed cooling water strainer | 1 | 1 | 15 | 30
3829-Other closed cooling water system problems A | 71 | 71 | 5884.98 | 56792.281
3830-Auxiliary boiler | 37 | 37 | 9221.46 | 338139.1821
3831-Auxiliary steam piping | 13 | 13 | 1714 | 13078.233
3832-Auxiliary steam valves | 43 | 43 | 10640.41 | 216980.7044
3833-Auxiliary steam controls and instruments | 18 | 18 | 3772.26 | 39580.9223
3834-Auxiliary boiler tube leaks | 10 | 10 | 1454.8 | 99437.4206
3835-Auxiliary boiler burner management system | 8 | 8 | 3098 | 20077.1161
3836-Steam Transfer to Other Unit | 131 | 133 | 9686.08 | 151711.3968
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 40 | 40 | 6427.74 | 314033.6627
3840-Service air compressors | 31 | 31 | 2888.4 | 26117.4359
3842-Service air valves | 3 | 3 | 1092 | 16856.8827
3844-Soot blowing air compressor and system | 5 | 5 | 707 | 3762.7664
3849-Other service air problems | 5 | 5 | 970.61 | 121346.7042
3850-Instrument air compressors | 70 | 70 | 8401.59 | 55190.8864
3851-Instrument air piping | 25 | 25 | 2714.82 | 29104.2896
3852-Instrument air valves | 11 | 11 | 917.42 | 7809.6204
3853-Instrument air dryers | 4 | 4 | 388.5 | 819.8
3859-Other instrument air problems | 27 | 27 | 8776.42 | 93421.3873
3860-Fire protection system pumps | 2 | 2 | 170.73 | 8155.7396
3861-Fire protection system piping | 20 | 20 | 1169.03 | 22877.1192
3862-Fire protection system valves | 11 | 11 | 1638.6 | 48980.5427
3863-Fire protection system fouling | 3 | 3 | 591.2 | 3538.1898
3864-Fire protection system instrumentation and controls | 87 | 87 | 6321.74 | 154015.8415
3869-Other fire protection system problems | 49 | 49 | 4817.46 | 205995.6143
3870-Fuel Gas Compressor and Motors | 40 | 40 | 3122.11 | 66247.3761
3871-Fuel Gas Compressor Piping | 6 | 6 | 301.9 | 2304.4599
3872-Fuel Gas Compressor Valves | 42 | 42 | 5707.32 | 123423.1057
3873-Fuel Gas Compressor Heat Exchangers | 5 | 5 | 475.76 | 5363.2552
3874-Fuel Gas Compressor Controls and Instrumentation | 92 | 93 | 5464.81 | 61595.4605
3875-Fuel Gas Compressor Filters | 8 | 8 | 794 | 1358.8829
3876-Fuel Gas Compressor Fire System | 1 | 1 | 45 | 8.25
3879-Fuel Gas Compressor - other | 95 | 96 | 4863.75 | 45164.9434
3880-Seal air fan | 5 | 5 | 271.41 | 1566.6504
3881-Seal air fan drive - motor | 2 | 2 | 79.83 | 2474.73
3889-Other seal air fan system problems | 2 | 2 | 178 | 1796.5
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 81 | 81 | 6057.63 | 70769.8911
3899-Other miscellaneous auxiliary system problems | 90 | 91 | 8730.68 | 134260.0169
3950-Process computer | 50 | 50 | 6737.36 | 25586.2296
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 195 | 198 | 3944.25 | 630905.2695
3970-Distributive Control System (DCS) - process computer | 62 | 62 | 9111.46 | 78527.6469
3971-DCS - data highway | 84 | 84 | 6546.51 | 46213.1795
3972-DCS - hardware problems (including card failure) | 169 | 169 | 29520 | 299695.0194
3973-DCS - internal and termination wiring | 25 | 25 | 2954.43 | 58031.2616
3974-DCS - logic problems | 117 | 117 | 20666.84 | 145860.1981
3975-DCS - upgrades | 6 | 6 | 667.03 | 18476.234
3979-Other DCS problems | 119 | 129 | 15140.63 | 131730.9365
3980-Programmable Logic Controller (PLC) | 31 | 31 | 2267.24 | 13598.8862
3981-PLC - data highway | 11 | 11 | 521.68 | 2211.3472
3982-PLC - hardware problems (including card failure) | 46 | 46 | 4331.9 | 77423.1301
3983-PLC - internal and termination wiring | 3 | 3 | 499 | 1336.5
3984-PLC - logic problems | 9 | 9 | 846.82 | 1581.1663
3985-PLC - upgrades | 2 | 2 | 18.13 | 35.577
3989-Other PLC problems | 11 | 11 | 1658.77 | 23222.6901
3995-Powerhouse heating and ventilating systems | 7 | 7 | 376 | 1579.5666
3996-Air conditioning systems - rooms and areas | 16 | 16 | 2339.36 | 7594.4916
3998-Balance of plant overhaul/outage | 21 | 21 | 1638.5 | 194903.4409
3999-Other miscellaneous balance of plant problems | 438 | 442 | 44749.83 | 3438645.6682
4000-Outer casing A | 5 | 5 | 1767 | 4565.9159
4001-Inner casing C | 2 | 2 | 239.27 | 179.3185
4010-Nozzles and nozzle blocks C | 3 | 3 | 506 | 51237.1997
4011-Diaphragms A | 12 | 12 | 333 | 219461.9666
4012-Buckets or blades A | 24 | 24 | 530 | 591455.8833
4014-Bucket or blade fouling C | 830 | 1089 | 9234.6 | 401743.0737
4015-Wheels or spindles A | 1 | 1 | 164 | 464.6666
4020-Shaft seals B | 2 | 2 | 399.91 | 20596.9432
4030-Rotor shaft C | 10 | 10 | 3246 | 308017.2321
4040-Bearings C | 211 | 214 | 19451.32 | 602844.4661
4041-HP steam turbine thrust bearings | 16 | 16 | 1055.91 | 46879.792
4099-Other high pressure turbine problems | 142 | 148 | 14229.55 | 440918.9755
4100-Outer casing B | 2 | 2 | 402.72 | 13703.6253
4110-Nozzles and nozzle blocks B | 1 | 1 | 600 | 270189.9996
4112-Buckets or blades B | 2 | 2 | 304 | 312859.0666
4113-Bucket or blade fouling B | 3 | 3 | 42 | 2706.4333
4120-Shaft seals C | 32 | 32 | 759.5 | 8180.6582
4130-Rotor shaft B | 1 | 1 | 42 | 297.5
4140-Bearings D | 18 | 18 | 6207.5 | 195315.0317
4199-Other intermediate pressure turbine problems | 52 | 52 | 26726.14 | 1484668.4982
4200-Outer casing C | 2 | 2 | 195 | 4238.7333
4211-Diaphragms C | 6 | 6 | 546 | 5232.3663
4212-Buckets or blades C | 72 | 73 | 1703 | 442916.2829
4213-Bucket or blade fouling A | 18 | 29 | 307 | 259401.6666
4220-Shaft seals D | 2 | 2 | 26 | 39171.3833
4222-Gland rings A | 2 | 2 | 542 | 29045.2999
4230-Rotor shaft A | 6 | 6 | 1214 | 1223269.5999
4240-Bearings E | 37 | 37 | 6498.73 | 386900.8223
4241-LP steam turbine thrust bearings | 4 | 4 | 692.3 | 101332.0432
4250-Other low pressure turbine problems | 83 | 83 | 9028.51 | 982703.4478
4260-Main stop valves | 123 | 124 | 28066.06 | 689095.8912
4261-Control valves | 446 | 447 | 70146.96 | 3223777.9628
4262-Intercept valves | 73 | 73 | 19460.15 | 305847.9224
4263-Reheat stop valves | 43 | 43 | 11727.98 | 506448.0832
4264-Combined intercept valves | 15 | 15 | 4990 | 167279.1326
4265-Miscellaneous drain and vent valves | 20 | 20 | 4057.6 | 129700.5608
4266-Main stop valve testing | 33 | 34 | 6674.94 | 96351.8322
4267-Control valve testing | 45 | 45 | 7546.64 | 16186.4098
4268-Reheat/intercept valve testing | 13 | 13 | 4846.45 | 28336.3705
4269-Other turbine valves (including LP steam admission valves) | 81 | 82 | 18260.94 | 1255342.436
4270-Crossover or under piping | 22 | 22 | 10206 | 621575.5968
4279-Miscellaneous turbine piping | 69 | 69 | 37822.8 | 1152313.7855
4280-Lube oil pumps A | 26 | 26 | 6978.98 | 418285.9638
4281-Lube oil coolers A | 21 | 21 | 5831.1 | 289760.6074
4282-Lube oil conditioners | 1 | 1 | 390 | 10074.9999
4283-Lube oil system valves and piping | 23 | 23 | 5975.68 | 376761.869
4284-Lube oil pump drive | 5 | 5 | 1086.44 | 78682.4364
4289-Other lube oil system problems | 78 | 78 | 17145 | 933007.4691
4290-Hydraulic system pumps | 12 | 12 | 4151.83 | 32350.5209
4291-Hydraulic system coolers | 6 | 6 | 1062 | 14257.8997
4292-Hydraulic system filters | 8 | 8 | 1697.66 | 6987.7804
4293-Hydraulic system pipes and valves | 94 | 94 | 22843.83 | 522435.0133
4299-Other hydraulic system problems | 91 | 92 | 22503.14 | 444532.8001
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 54 | 54 | 10856.51 | 83354.7676
4301-Turbine governing system | 124 | 124 | 16879.71 | 670028.8718
4302-Turbine trip devices (including instruments) | 188 | 189 | 45011.85 | 642557.8418
4303-Exhaust hood and spray controls | 10 | 10 | 2955.36 | 27911.0069
4304-Automatic turbine control systems - mechanical | 11 | 11 | 2348.96 | 12839.0973
4305-Automatic turbine control systems - mechanical - hydraulic | 13 | 13 | 2352.52 | 12010.8255
4306-Automatic turbine control systems - electro-hydraulic - analog | 7 | 7 | 1757.9 | 22856.3274
4307-Automatic turbine control systems - electro-hydraulic - digital | 24 | 24 | 8182.03 | 215924.7602
4308-Automatic turbine control systems - digital control and monitoring | 46 | 46 | 7028.41 | 988984.0971
4309-Other turbine instrument and control problems | 126 | 126 | 23846.72 | 273531.9347
4310-Steam Turbine Control System - data highway | 5 | 5 | 1499.7 | 110410.4895
4311-Steam Turbine Control System - hardware problems (including card failure) | 59 | 59 | 11722.48 | 971609.8158
4312-Steam Turbine Control System - internal and termination wiring | 5 | 5 | 713 | 125568.2663
4313-Steam Turbine Control System - logic problems | 44 | 45 | 12908.76 | 75414.8525
4314-Steam Turbine Control System - upgrades | 5 | 5 | 1638.7 | 9245.3628
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 21 | 21 | 4702.37 | 1014975.8493
4401-Inspection F | 4 | 4 | 786 | 162523.8998
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 2 | 2 | 144 | 3744.3166
4410-Turning gear and motor A | 60 | 60 | 11519.87 | 379701.5743
4411-Steam turbine gear box (single shaft configuration) | 3 | 3 | 95 | 101684.3333
4412-Steam turbine clutch (single shaft configuration) | 1 | 1 | 242 | 13814.1666
4415-Shaft coupling mechanism | 1 | 1 | 340 | 65376.3332
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 196 | 210 | 38667.46 | 968092.2859
4430-Gland seal system | 62 | 62 | 9912.51 | 367639.0502
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 7 | 7 | 1715.71 | 21994.1212
4450-Water induction | 18 | 18 | 2289 | 479802.9961
4460-Turbine overspeed trip test | 10 | 10 | 2253 | 7227.7325
4470-Differential expansion | 99 | 99 | 24641.15 | 329666.4691
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 4 | 4 | 175.56 | 691.0435
4499-Other miscellaneous steam turbine problems | 327 | 344 | 56370.35 | 3938864.4705
4500-Rotor windings (including damper windings and fan blades on hydro units) | 57 | 58 | 9618.24 | 2834168.2003
4510-Rotor collector rings | 14 | 14 | 3106.08 | 621788.5394
4511-Rotor; General | 30 | 30 | 3748.4 | 1027138.3812
4520-Stator windings; bushings; and terminals | 58 | 58 | 9311.54 | 9093356.5623
4530-Stator core iron | 1 | 1 | 77 | 50097.4833
4535-Stator; General | 48 | 51 | 10017.27 | 1701762.6497
4536-Generator heaters | 1 | 1 | 52.8 | 12755.6
4540-Brushes and brush rigging | 47 | 47 | 6314.26 | 393636.0798
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 144 | 144 | 16043.52 | 1868346.9907
4551-Generator bearings | 55 | 55 | 6014.2 | 969702.1108
4552-Generator lube oil system | 72 | 72 | 4230.38 | 43577.1554
4555-Bearing cooling system A | 41 | 41 | 3558.55 | 269920.5698
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 160 | 160 | 14196.01 | 878060.3902
4570-Generator casing | 8 | 8 | 1655.92 | 473705.7013
4580-Generator end bells and bolting | 3 | 3 | 1058 | 30061.4161
4590-Generator brakes | 36 | 36 | 3439.63 | 29612.6672
4600-Exciter drive - motor | 13 | 13 | 1275.47 | 19647.4972
4601-Exciter field rheostat | 30 | 30 | 3281.87 | 263209.8336
4602-Exciter commutator and brushes | 38 | 38 | 3575.86 | 220116.5853
4603-Solid state exciter element | 62 | 62 | 8770.99 | 342068.2849
4604-Exciter drive - shaft | 13 | 13 | 1401.02 | 182269.5114
4605-Exciter transformer | 29 | 29 | 3671.33 | 231833.298
4609-Other exciter problems | 632 | 636 | 101298.01 | 7568514.4814
4610-Hydrogen cooling system piping and valves | 34 | 34 | 11444.93 | 624123.4933
4611-Hydrogen coolers | 50 | 50 | 6008.81 | 374443.1553
4612-Hydrogen storage system | 4 | 4 | 346.72 | 3776.2415
4613-Hydrogen seals | 12 | 12 | 3609.4 | 210660.5243
4619-Other hydrogen system problems | 29 | 29 | 7140.14 | 157618.3124
4620-Air cooling system | 48 | 48 | 6329.03 | 71979.9246
4630-Liquid cooling system | 64 | 64 | 10149.72 | 120472.2926
4640-Seal oil system and seals A | 32 | 32 | 7881.12 | 409122.445
4650-Other cooling system problems | 51 | 51 | 9859.26 | 224241.6986
4700-Generator voltage control | 197 | 197 | 34727.57 | 857907.3399
4710-Generator metering devices | 54 | 54 | 8536.35 | 135504.9453
4720-Generator synchronization equipment | 226 | 230 | 20629.94 | 357868.0691
4730-Generator current and potential transformers | 106 | 106 | 18868.48 | 395262.0677
4740-Emergency generator trip devices | 370 | 372 | 95422.64 | 2263393.1445
4750-Other generator controls and metering problems | 269 | 270 | 33471.81 | 1056352.1458
4800-Generator main leads | 28 | 28 | 5984.74 | 1971946.1185
4805-Generator Bus Duct Cooling System | 51 | 51 | 8248.5 | 52072.2224
4810-Generator output breaker | 357 | 368 | 35005.46 | 2041129.5456
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 812.87 | 138357.6798
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 4 | 4 | 1763.74 | 678060.1798
4840-Inspection E | 19 | 19 | 1826.5 | 118310.9609
4842-Reactive and capability testing | 42 | 42 | 4304.98 | 384320.243
4850-Core monitor alarm | 1 | 1 | 173.7 | 156.33
4860-Generator Neutral Grounding Equipment | 47 | 47 | 8180.77 | 348561.8424
4899-Other miscellaneous generator problems | 364 | 364 | 47548.63 | 4608345.0316
5000-Inlet air ducts A | 18 | 18 | 1376.4 | 20336.9762
5001-Inlet air vanes / nozzles | 140 | 140 | 16244.44 | 259847
5002-Inlet air filters A | 77 | 77 | 6300.28 | 194781.8592
5003-Inlet cone | 2 | 2 | 110 | 156.1666
5004-Inlet air chillers B | 158 | 171 | 1365.79 | 88265.6383
5005-Inlet air evaporative coolers B | 36 | 36 | 1915.06 | 19865.4807
5006-Inlet air foggers B | 11 | 11 | 156 | 15756.8733
5009-Other inlet air problems A | 93 | 93 | 9465.49 | 51902.3034
5010-High pressure shaft D | 3 | 3 | 224.8 | 8355.1415
5011-High pressure bearings C | 1 | 1 | 55 | 1707.75
5012-High pressure blades/buckets B | 14 | 14 | 1814.98 | 579337.9781
5013-Compressor casing and bolts | 3 | 3 | 305 | 1285.5166
5014-Compressor diaphragms | 9 | 9 | 991.5 | 91758.8846
5015-Compressor seals | 2 | 2 | 185 | 311.9166
5016-High pressure compressor bleed valves | 152 | 152 | 19939.06 | 186426.9738
5017-Low pressure compressor bleed valves | 87 | 105 | 9138.71 | 53580.9261
5019-Other high pressure problems A | 15 | 15 | 1998.7 | 49881.3058
5020-Low pressure shaft D | 1 | 1 | 183 | 87657
5021-Low pressure bearings D | 1 | 1 | 47.5 | 373.6666
5022-Low pressure blades/buckets A | 9 | 9 | 936.7 | 193030.3963
5029-Other low pressure problems E | 9 | 9 | 565 | 33392.4663
5035-Compressor Washing | 28 | 28 | 1770.5 | 6714.1694
5037-Inlet bleed heat valve | 22 | 22 | 3599.76 | 12151.7804
5039-Other compressor problems | 109 | 110 | 9621.32 | 1079673.1486
5040-Fuel tanks B | 22 | 22 | 362.54 | 1583.5922
5041-Fuel piping and valves A | 681 | 689 | 86567.27 | 641093.3126
5042-Fuel nozzles/vanes B | 77 | 77 | 8175.29 | 187319.8118
5043-Fuel filters A | 38 | 38 | 5527.7 | 27230.6078
5044-Liquid fuel oil pump A | 18 | 18 | 809.92 | 53293.9964
5046-Liquid fuel oil transfer/forwarding pump B | 26 | 26 | 3757.02 | 21368.1985
5047-Liquid fuel purge system A | 43 | 43 | 4878.8 | 20205.5357
5048-Gas fuel system B | 609 | 623 | 68923.86 | 1171357.128
5049-Other fuel system problems B | 316 | 316 | 35073.69 | 523501.0075
5050-Ignition system A | 336 | 345 | 44086.93 | 323604.8667
5051-Pilot fuel piping and valves A | 137 | 150 | 15839.62 | 70282.3414
5052-Pilot fuel nozzles/vanes B | 9 | 9 | 968.5 | 25665.6914
5053-Pilot fuel filters A | 1 | 1 | 85 | 9.9166
5054-Water Injection System (Gas Turbine) | 126 | 126 | 8971.76 | 349386.8625
5060-Atomizing air system B | 52 | 52 | 6805.42 | 54413.466
5065-NOx water injection system including pumps | 116 | 116 | 5824.33 | 56750.2623
5066-NOx Steam Injection System | 29 | 29 | 5669.79 | 36004.7739
5070-Combustor casing A | 8 | 8 | 1096.06 | 74332.9722
5071-Combustor liner B | 21 | 21 | 2399.95 | 357385.0611
5072-Combustor caps B | 10 | 10 | 2045.02 | 82528.3785
5073-Flame scanners B | 114 | 115 | 11722.94 | 55665.043
5074-Flashback including instruments | 58 | 58 | 6415.59 | 46447.9886
5075-Blade Path Temperature Spread A | 253 | 258 | 40560.76 | 489465.1132
5079-Other combustor problems B | 297 | 304 | 39525.36 | 562512.8665
5080-High pressure shaft C | 9 | 9 | 1115.3 | 263267.7112
5081-High pressure bearings D | 14 | 14 | 1440.4 | 71947.0064
5082-High pressure blades/buckets A | 17 | 17 | 2648.4 | 1318304.2258
5083-High pressure nozzles/vanes A | 16 | 16 | 1413.61 | 1262789.0795
5084-High pressure casing/expansion joints | 3 | 3 | 366.3 | 18826.7932
5086-High pressure shaft seals A | 1 | 1 | 65 | 1093.0833
5087-Thrust Bearing | 1 | 1 | 513.2 | 547.413
5088-Gas turbine cooling steam | 23 | 23 | 5260.5 | 61379.7733
5089-Other high pressure problems B | 9 | 9 | 689.66 | 1745.7571
5091-Low pressure bearings A | 7 | 7 | 1168.48 | 64878.9715
5092-Low pressure blades/buckets D | 12 | 12 | 1641.75 | 666022.8201
5093-Low pressure nozzles/vanes B | 7 | 7 | 936 | 4790.5329
5094-Low pressure casing/expansion joints A | 10 | 10 | 1404 | 9319.3996
5095-Interstage gas passages ? LP | 3 | 3 | 425 | 597.4832
5096-Low pressure shaft seals | 1 | 1 | 55 | 117.3333
5097-Other low pressure problems B | 16 | 16 | 1334.8 | 15352.5442
5098-Expansion joints A | 1 | 1 | 45 | 2352
5100-Chamber A | 4 | 4 | 683 | 5821.2498
5101-Hoods B | 4 | 4 | 446 | 1547
5102-Vanes/nozzles A | 1 | 1 | 27 | 8.1
5103-Silencer B | 5 | 5 | 837 | 114847.4664
5104-Cones A | 1 | 1 | 165 | 16494.4999
5105-Diverter Dampers B | 14 | 15 | 1075.4 | 13811.0311
5106-Exhaust Stack | 10 | 10 | 1079.42 | 30299.5442
5108-High engine exhaust temperature A | 126 | 126 | 18133.4 | 637531.6264
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 190 | 191 | 23732.21 | 467242.6683
5110-Lube oil system - general | 233 | 233 | 17946.65 | 429245.0541
5111-Lube oil pumps B | 91 | 91 | 10641.24 | 179135.9395
5112-Lube oil coolers B | 25 | 25 | 2587.34 | 59044.3584
5113-Lube oil valves/piping | 33 | 33 | 4156.14 | 311714.1534
5114-Lube oil filters | 9 | 9 | 655.9 | 3172.9447
5115-Oil vapor extractor | 44 | 51 | 3945.1 | 25033.1775
5116-Power Augmentation System Equipment B | 23 | 23 | 1113.13 | 8140.08
5117-Power augmentation piping | 3 | 3 | 42 | 895.1666
5118-Power augmentation valves | 8 | 8 | 477.65 | 10672.8156
5119-Power augmentation controls | 3 | 3 | 517 | 1085.6997
5120-Hydraulic oil system A | 123 | 123 | 13497.39 | 477345.2897
5121-Hydraulic oil system pumps | 15 | 15 | 1323.84 | 9805.1911
5122-Hydraulic oil system piping/valves | 42 | 42 | 4442.07 | 86606.4432
5130-Starting system (including motor) A | 374 | 374 | 48143.36 | 1145687.8245
5140-Battery and charger system B | 19 | 19 | 1544.47 | 39172.2806
5150-Turning gear and motor C | 86 | 86 | 9816.54 | 595776.588
5151-Load gear compartment B | 7 | 7 | 453.55 | 8322.4998
5160-Cooling and seal air system B | 147 | 147 | 23660.94 | 316660.5951
5170-Cooling water system A | 69 | 70 | 7612.79 | 123151.0563
5180-Anti-icing system A | 17 | 17 | 1600.15 | 39575.202
5190-Other auxiliary system problems A | 104 | 104 | 10683.94 | 258069.9778
5200-Reduction gear B | 7 | 7 | 184 | 77284.4
5201-Load shaft and bearings A | 19 | 19 | 2443.4 | 59357.1775
5205-Main coupling between the turbine and generator A | 2 | 2 | 84.09 | 1967.4904
5206-Gas Turbine Clutch | 26 | 28 | 2059.05 | 38773.1452
5210-Intercoolers A | 14 | 14 | 988 | 10979.033
5230-Heat shields C | 2 | 2 | 379 | 3859.4832
5240-Fire detection and extinguishing system B | 177 | 178 | 23043.15 | 777702.3043
5241-Fire in unit A | 8 | 8 | 776.9 | 352205.3532
5245-Gas Turbine Control System - data highway | 75 | 75 | 7529.57 | 39247.937
5246-Gas Turbine Control System - hardware problems (including card failure) | 281 | 283 | 33888.86 | 397687.2513
5247-Gas Turbine Control System - internal and termination wiring | 45 | 45 | 4472.53 | 89261.3421
5248-Gas Turbine Control System - logic problems | 115 | 115 | 14414.04 | 83543.7343
5249-Gas Turbine Control System - upgrades | 21 | 21 | 3155.51 | 27364.4738
5250-Other Controls and instrumentation Problems A | 523 | 525 | 66710.07 | 518687.3651
5255-Computer | 13 | 13 | 1366.4 | 10348.818
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 3 | 3 | 317.04 | 266960.8392
5261-Gas turbine/compressor washing | 21 | 21 | 2319.62 | 20548.6611
5262-Gas turbine exchange | 3 | 3 | 179.7 | 3297.4949
5269-Combustion inspection (CI) | 1 | 1 | 163 | 19646.9333
5270-Hot end inspection B | 9 | 9 | 1542.93 | 59045.2545
5272-Boroscope inspection A | 20 | 20 | 2334.75 | 388976.1833
5274-General unit inspection A | 33 | 33 | 1335.25 | 260879.3314
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 53 | 53 | 3479.68 | 186942.3547
5285-Gas turbine vibration | 266 | 327 | 27171.95 | 2277640.7588
5286-Gas Turbine lockout cause by OEM specifications | 4 | 4 | 443 | 4123.6165
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 36 | 52 | 1156.55 | 3703.8617
5295-Synchronous condenser equipment A | 2 | 2 | 675 | 19769.5829
5298-Main gas filter | 4 | 4 | 667.5 | 3862.0913
5299-Other miscellaneous gas turbine problems | 468 | 472 | 51617.68 | 1896220.148
5400-Inlet air ducts B | 7 | 7 | 285.9 | 1221.4815
5401-Inlet air vanes/noozles | 25 | 25 | 1680.04 | 22274.0416
5402-Inlet air filters B | 20 | 20 | 762.1 | 2208.9601
5404-Inlet air chillers A | 62 | 63 | 491.61 | 61828.5034
5405-Inlet air evaporative coolers A | 1 | 1 | 4 | 39.6
5406-Inlet air foggers A | 4 | 4 | 103 | 2450.6333
5409-Other inlet air problems B | 30 | 31 | 2053.8 | 25223.5262
5410-High pressure shaft B | 1 | 1 | 46.55 | 13359.85
5412-High pressure blades/buckets C | 4 | 4 | 24.2 | 91.6233
5413-Other high pressure problems D | 11 | 11 | 535.74 | 16604.9661
5414-Compressor diaphragms/vanes | 4 | 4 | 270.7 | 7077.56
5420-Low pressure shaft C | 1 | 1 | 45 | 20.25
5421-Low pressure bearings B | 1 | 1 | 48 | 2783.2
5422-Low pressure blades/buckets C | 2 | 2 | 56 | 6826.3
5429-Other low pressure problems D | 5 | 5 | 163 | 49655.0166
5435-Jet Engine Compressor Washing | 1 | 1 | 45 | 67.5
5439-Jet engine other compressor problems | 13 | 13 | 561.36 | 41660.0999
5440-Fuel tanks A | 5 | 5 | 192.32 | 126.5026
5441-Fuel piping and valves B | 109 | 109 | 4180.26 | 38756.8566
5442-Fuel nozzles/vanes A | 4 | 4 | 152.8 | 290.2967
5443-Fuel filters B | 12 | 13 | 545.4 | 2932.5332
5444-Liquid fuel oil pump B | 7 | 7 | 238.6 | 1775.4799
5445-Liquid fuel oil transfer/forwarding pump A | 3 | 3 | 59 | 81.3166
5446-Liquid fuel purge system B | 2 | 2 | 108.4 | 234.8666
5447-Gas fuel system A | 147 | 148 | 6287 | 348714.9785
5449-Other fuel system problems A | 132 | 135 | 4899.69 | 35347.3997
5450-Ignition system B | 44 | 46 | 2247.36 | 24131.3418
5451-Pilot fuel piping and valves B | 5 | 5 | 224.69 | 2301.3821
5452-Pilot fuel nozzles/vanes A | 3 | 3 | 510 | 4368.9998
5454-Water injection system (Jet Engine) | 82 | 84 | 3795.5 | 31357.7761
5455-Fuel nozzle/vane cooling air system | 3 | 3 | 91.4 | 302.9966
5460-Atomizing air system A | 9 | 9 | 287.5 | 8913.2832
5471-Combustor liner A | 2 | 2 | 72 | 50849.0167
5473-Flame scanners A | 27 | 27 | 1757.65 | 9636.3965
5475-Blade Path Temperature Spread B | 52 | 53 | 7125.05 | 90005.4088
5479-Other combustor problems A | 35 | 36 | 1460.34 | 33881.9996
5480-High pressure shaft A | 2 | 2 | 83.3 | 654.355
5481-High pressure bearings A | 3 | 3 | 70 | 20655.1666
5482-High pressure blades/buckets D | 9 | 11 | 391.56 | 341118.8787
5483-High pressure nozzles/vanes B | 6 | 6 | 212 | 166804.8499
5487-Thrust Bearing/jet | 1 | 1 | 45 | 19.5
5489-Other high pressure problems C | 14 | 14 | 674.6 | 9579.9998
5491-Low pressure bearings C | 1 | 1 | 46 | 4578.5333
5492-Low pressure blades/buckets B | 9 | 9 | 249 | 60866.5499
5497-Other low pressure problems C | 7 | 7 | 332 | 200.4165
5500-Chamber B | 1 | 1 | 95 | 372.0833
5502-Vanes/nozzles B | 2 | 2 | 93 | 16016.1
5504-Cones B | 2 | 2 | 269.6 | 23598.9866
5505-Diverter Dampers A | 3 | 3 | 139.83 | 345.49
5508-High engine exhaust temperature B | 37 | 37 | 1570.4 | 21138.3863
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 16 | 16 | 966.54 | 49700.5531
5510-Lube oil system A | 166 | 166 | 7360.61 | 158611.8453
5516-Power Augmentation System Equipment A | 27 | 27 | 498.9 | 2861.1619
5520-Hydraulic oil system B | 26 | 26 | 1386.26 | 57689.5729
5530-Starting system (including motor) B | 56 | 56 | 3550.1 | 42912.1642
5540-Battery and charger system A | 3 | 3 | 118 | 934.0666
5550-Turning gear and motor B | 6 | 6 | 160.3 | 24451.21
5560-Cooling and seal air system A | 26 | 26 | 1100 | 32525.7563
5570-Cooling water system B | 14 | 14 | 426.7 | 3988.9332
5580-Anti-icing system B | 10 | 10 | 449.9 | 1907.5648
5590-Other auxiliary system problems B | 67 | 67 | 2472.96 | 39786.316
5600-Reduction gear A | 2 | 2 | 82.24 | 2504.29
5605-Main coupling between the turbine and generator B | 2 | 2 | 134.26 | 401.64
5606-Jet Engine Clutch | 8 | 8 | 406 | 4353.8165
5610-Intercoolers B | 5 | 5 | 266.5 | 13646.5498
5620-Regenerators B | 17 | 17 | 340 | 101911.3332
5640-Fire detection and extinguishing system A | 33 | 33 | 1606.69 | 35695.2362
5641-Fire in unit B | 1 | 1 | 52 | 3854.9333
5645-Jet Engine Control System - data highway | 28 | 28 | 1187.93 | 6452.8704
5646-Jet Engine Control System - hardware problems (including card failure) | 92 | 92 | 3743.34 | 41163.7076
5647-Jet Engine Control System - internal and termination wiring | 12 | 12 | 603.2 | 17732.9631
5648-Jet Engine Control System - logic problems | 24 | 24 | 1013.38 | 6084.1084
5649-Jet Engine Control System - upgrades | 13 | 13 | 657.62 | 24882.5406
5650-Other Controls and instrumentation Problems B | 167 | 171 | 6804.43 | 72880.6459
5661-Engine/compressor washing | 6 | 6 | 422 | 3083.9832
5662-Engine exchange | 3 | 3 | 147 | 9394.9333
5665-Engine shafts and bearings | 4 | 4 | 190 | 42999.5166
5670-Hot end inspection A | 1 | 1 | 171 | 25402.05
5672-Boroscope inspection B | 3 | 3 | 135 | 1647.9
5674-General unit inspection B | 8 | 8 | 274 | 541.5833
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 41 | 44 | 1525.8 | 4283.7478
5685-Engine vibration | 112 | 114 | 4534.43 | 208547.6634
5686-Jet Engine lockout cause by OEM specifications | 10 | 10 | 399.18 | 1835.1652
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 5 | 5 | 34 | 193.6
5695-Synchronous condenser equipment B | 1 | 1 | 25 | 317.0833
5699-Other miscellaneous jet engine problems | 56 | 56 | 2141.53 | 14617.4797
5710-Cylinders | 5 | 5 | 46 | 44.8667
5711-Cylinder heads | 23 | 28 | 391.84 | 32520.5993
5740-Turbo charger | 2 | 2 | 6 | 5513.3
5799-Other engine problems | 10 | 20 | 349.61 | 1964.1393
5800-Lube oil system C | 2 | 2 | 22.57 | 51657.1508
5805-Cooling system | 12 | 12 | 83.69 | 5012.2593
5815-Fuel system | 12 | 13 | 174.75 | 3055.0124
5820-Start system | 10 | 11 | 87.6 | 149.26
5849-Other engine auxiliaries problems | 2 | 2 | 18.08 | 89.7973
5855-Engine control system | 20 | 20 | 129.64 | 1891.0755
5870-Other engine control problems | 1 | 1 | 2.57 | 65.6207
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 42 | 157 | 790.25 | 9309.9813
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 54 | 54 | 8142.26 | 118185.9329
6005-HP Evaporator tubes | 16 | 16 | 2079.11 | 168111.7446
6006-IP Evaporator tubes | 5 | 5 | 651 | 27080.3498
6007-LP Evaporator tubes | 5 | 5 | 587 | 37544.0666
6010-HP superheater | 29 | 29 | 4131.93 | 365497.9729
6011-HP reheater | 13 | 13 | 2761 | 126860.5662
6012-HP economizer | 33 | 33 | 3676.8 | 339059.5957
6020-IP superheater | 5 | 5 | 740.1 | 31992.8849
6021-IP reheater | 13 | 13 | 2649 | 197371.3575
6022-IP economizer | 2 | 2 | 270 | 2106
6032-LP economizer | 8 | 8 | 1356.4 | 91436.7128
6090-Other HRSG tube Problems | 26 | 26 | 4411.55 | 217211.1395
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 17 | 17 | 2092 | 22230.1159
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 25 | 25 | 5473 | 179051.3484
6111-HP steam relief/safety valves | 3 | 3 | 108 | 2010.5
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 22 | 23 | 3950 | 33299.064
6113-Other HP steam system problems | 21 | 21 | 3898.09 | 92653.8474
6114-HP steam isolation/boundary valves | 19 | 19 | 4368.26 | 271242.0652
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 1 | 1 | 472 | 9841.2
6121-IP steam relief/safety valves | 2 | 2 | 96.8 | 742.5
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 2 | 2 | 318 | 127.2
6123-Other IP steam system problems | 7 | 7 | 2005.7 | 273499.5027
6124-IP steam isolation/boundary valves | 2 | 2 | 609.36 | 6320.7104
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 3 | 3 | 556 | 5310.3331
6133-Other LP steam system problems | 18 | 18 | 2502.87 | 92335.0179
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 72 | 72 | 14131.74 | 355023.3418
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 3 | 3 | 541 | 12336.3163
6141-HP Desuperheater/attemperator valves | 29 | 29 | 5215.69 | 64526.0358
6142-HP Desuperheater/attemperator spray nozzles | 6 | 6 | 861 | 25012.4664
6144-Other HP desuperheater/attemperator problems | 14 | 14 | 2289 | 12905.0161
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 1 | 1 | 332 | 40802.8
6146-IP Desuperheater/attemperator valves | 3 | 3 | 291 | 250.5499
6147-IP Desuperheater/attemperator spray nozzles | 1 | 1 | 36 | 360
6148-IP Desuperheater/attemperator drums | 1 | 1 | 376.26 | 100.3357
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 6 | 6 | 1228 | 175010.8165
6161-HP Startup bypass system valves | 34 | 34 | 5478.73 | 73865.5394
6163-Other HP startup bypass system problems | 2 | 2 | 174 | 3423.6999
6164-HP Startup bypass instrumentation and controls | 45 | 45 | 7944.12 | 106481.0031
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 6 | 6 | 956 | 24544.8997
6171-IP Startup bypass system valves | 14 | 14 | 4438.36 | 71444.1844
6173-Other IP startup bypass system problems | 2 | 2 | 580 | 437.0666
6174-IP Startup bypass instrumentation and controls | 28 | 28 | 4798.16 | 80481.1939
6181-LP Startup bypass system valves | 3 | 3 | 571 | 878.2998
6184-LP startup bypass instrumentation and controls | 3 | 3 | 350.21 | 1134.8765
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 113 | 113 | 19945.24 | 348297.855
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 104 | 104 | 13759.59 | 199304.2963
6399-Other coal gasification equipment problems | 6 | 6 | 1485 | 9565.8329
6410-Steam wells/steam field piping problems | 6 | 6 | 56 | 140.8833
6460-Condenser problems due to H2S abatement system | 23 | 28 | 96 | 1077.8833
6499-Geothermal | 24 | 26 | 591 | 2158.5998
7000-Shaft B | 3 | 3 | 66.5 | 7988.6291
7001-Shaft packing | 33 | 33 | 3555.45 | 124264.8844
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 37 | 38 | 2007.72 | 120651.5881
7007-Bearings A | 38 | 38 | 2899.54 | 261191.9462
7008-Bearing cooling system B | 34 | 34 | 1755.73 | 17387.249
7009-Bearing Oil System | 70 | 70 | 7255.74 | 152956.9989
7010-Runner cavitation damage | 7 | 7 | 646.07 | 95553.0542
7011-Other runner problems | 8 | 8 | 218 | 232066.5166
7012-Casing; wear ring; or liner cavitation damage | 4 | 4 | 810 | 231824.0664
7014-Blade or bucket cracking | 6 | 6 | 559.55 | 53491.038
7020-Nozzle assembly | 1 | 1 | 61.94 | 3124.873
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 19 | 19 | 1460.99 | 501795.6473
7050-Turbine governor | 288 | 290 | 21812.21 | 1157274.6627
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 55 | 55 | 5227.26 | 1583272.9654
7053-Governor Oil System | 92 | 94 | 8018.55 | 85250.0644
7099-Other turbine problems | 203 | 219 | 11136.39 | 978952.0292
7100-Upper reservoir dams and dikes | 22 | 22 | 1191.59 | 26865.1164
7101-Lower reservoir dams and dikes | 5 | 5 | 428 | 3964.1581
7110-Intake channel or flume (including trash racks) | 59 | 62 | 3958.36 | 47248.5149
7111-Intake tunnel | 31 | 31 | 3816.7 | 362804.2821
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 58 | 59 | 977.49 | 26093.1915
7120-Headgates | 31 | 31 | 1877.09 | 139842.854
7121-Shutoff valves | 40 | 40 | 5258.81 | 200773.5602
7123-Shutoff valve bypass line and valve | 7 | 7 | 1600.7 | 17639.226
7124-Penstock | 17 | 17 | 808.64 | 11973.1523
7130-Spiral case | 7 | 7 | 374.9 | 22896.8066
7140-Wicket gate assembly | 23 | 23 | 1157.9 | 178549.0015
7141-Wicket gate operating mechanism or positioner | 24 | 24 | 2560.57 | 32672.5559
7142-Wicket gate shear pin | 148 | 148 | 9380.11 | 265315.5748
7160-Pressure regulating valve | 3 | 3 | 57 | 20209
7161-Pressure regulating valve operator or positioner | 2 | 2 | 157.9 | 277.6408
7162-Relief valve and vacuum breakers | 3 | 3 | 324.65 | 19834.339
7170-Draft tube | 8 | 8 | 675.31 | 10275.5923
7180-Tailrace | 25 | 25 | 976.48 | 27001.0175
7181-Tail water depressing equipment | 21 | 21 | 2093.25 | 25787.1212
7190-Dewatering and rewatering equipment | 2 | 2 | 244.02 | 2950.8232
7191-Equalizing line | 2 | 2 | 794 | 14698.3498
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 188 | 196 | 2478.81 | 275511.5872
7201-Inspection A | 4 | 4 | 364.68 | 67557.2325
7210-Canals (including siphons; radial gates; and spills) | 4 | 4 | 168.5 | 10457.3666
7240-Powerhouse Substructure | 7 | 7 | 393.72 | 11043.219
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 43 | 43 | 5064.56 | 193902.3591
7800-Couplings | 1 | 1 | 85.9 | 2705.85
7820-Bearings B | 16 | 16 | 914 | 70243.9664
7830-Blades | 10 | 10 | 81 | 74665.5
7840-Discs | 1 | 1 | 13 | 58.0667
7860-Nozzles/vanes | 2 | 2 | 93 | 1502.7667
7900-Inner casing D | 1 | 1 | 31 | 3357.3
7910-Outer exhaust casing | 6 | 6 | 198.7 | 52503.2933
7920-Lube oil system B | 7 | 7 | 507.4 | 28659.8432
7930-Controls and instrumentation A | 24 | 24 | 1586.26 | 68516.3203
7940-Evactor | 1 | 1 | 50 | 85
7960-Other expander turbine problems | 8 | 8 | 398.4 | 37867.5216
8000-Chemical feed storage; mill feeders; and conveyors | 5 | 5 | 1284 | 13818.8831
8006-Weigh feeders | 2 | 2 | 272.33 | 1092.6931
8010-Crushers/mills | 148 | 149 | 23891.72 | 747702.1688
8020-Mill slurry tanks supply problems | 16 | 16 | 4578 | 126491.9481
8030-Classifiers | 1 | 1 | 137 | 411
8040-Slurry transfer pumps and motors | 11 | 11 | 1403.23 | 3069.5756
8050-Chemical unavailability | 3 | 3 | 1023 | 31686.9993
8099-Other chemical supply problems | 2 | 2 | 286.55 | 487.1199
8100-Scrubber/absorber tower or module | 46 | 47 | 5724.55 | 733399.9861
8110-Spray nozzles | 16 | 16 | 2490 | 72324.9326
8120-Spray pumps and motors | 16 | 16 | 2687 | 23044.466
8125-Scrubber recycle (liquid) pumps | 26 | 26 | 4109.95 | 21770.776
8127-Scrubber recycle (liquid) pump motors | 5 | 5 | 1030 | 7359.6662
8130-Recirculation tanks including agitators | 9 | 9 | 629.3 | 19708.4748
8140-Reaction tanks including agitators | 7 | 7 | 1265.67 | 40021.2754
8150-Tubes | 8 | 8 | 1232.34 | 88854.0165
8160-Mist eliminators/demisters and washdown | 30 | 30 | 2690.07 | 182413.9733
8199-Other scrubber problems | 67 | 67 | 6379.84 | 106391.3027
8200-Piping | 26 | 26 | 5629.69 | 173806.5222
8210-Valves | 14 | 14 | 3362.4 | 51703.9012
8220-Strainers or filters | 41 | 42 | 3166 | 57297.6491
8230-Ducting | 27 | 27 | 4499.55 | 487849.6654
8235-Demister | 13 | 13 | 297 | 67.9499
8240-Bypass dampers | 17 | 18 | 2923.09 | 44239.4308
8250-Dampers other than bypass | 8 | 8 | 1381.68 | 20562.2414
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 142 | 142 | 24078.88 | 1784098.1354
8261-Scrubber booster I.D. fan drive | 12 | 12 | 1562.5 | 37548.8247
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 20 | 20 | 5639 | 266046.3815
8265-Scrubber ID fan dampers | 2 | 2 | 600 | 8306.4996
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 20 | 20 | 4913.26 | 30953.2758
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 3 | 3 | 509.92 | 5606.3033
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 7 | 7 | 288.88 | 20930.75
8275-Scrubber FD fan dampers | 2 | 2 | 548 | 11500.4165
8280-Reagent feed piping | 19 | 19 | 3411.05 | 60535.5583
8299-Other piping; ducting; damper; and fan problems | 19 | 19 | 2867.5 | 28589.491
8325-Ash disposal problems | 8 | 8 | 559 | 21662.9999
8330-Dewatering equipment (thickener; centrifuge; etc.) | 45 | 45 | 17269.62 | 1341030.7128
8340-Centrifuge/vacuum filter | 1 | 1 | 119 | 1128.5166
8349-Other waste disposal and recovery problems | 1 | 1 | 430 | 6306.6664
8399-Solids conveying and mixing system problems | 2 | 2 | 526.57 | 5373.8231
8400-Scrubber gas discharge reheaters - general | 1 | 1 | 87 | 775.7499
8410-Scrubber instruments and controls | 10 | 10 | 1477.75 | 9139.1805
8415-Liquid level controls | 4 | 4 | 103 | 3243.6333
8425-Miscellaneous mechanical failures | 3 | 3 | 160.95 | 6087.9949
8426-Miscellaneous electrical failures | 13 | 13 | 1529.84 | 6944.0794
8460-Testing | 3 | 3 | 251 | 1210.7832
8499-Other miscellaneous wet scrubber problems | 227 | 227 | 7684.88 | 558398.1455
8500-Slurry storage and feed tanks | 3 | 3 | 645 | 16405.1332
8501-Reagent storage; feed bins; and conveyors | 1 | 1 | 10 | 43.6667
8502-Weigh feeders | 1 | 1 | 76 | 1361.6666
8503-Screw conveyors | 1 | 1 | 5 | 343.5
8504-Mills/slakers | 1 | 1 | 35 | 104.4167
8506-Slurry pipelines | 9 | 9 | 1565 | 11858.8324
8510-Slurry mixers and agitators | 1 | 1 | 10 | 96.1667
8520-Slurry transfer pumps and motors | 3 | 3 | 416 | 588.1332
8521-Reagent/slurry problems | 43 | 43 | 5219.7 | 65062.4397
8522-Piping | 12 | 12 | 2186.92 | 50037.124
8523-Valves | 7 | 7 | 1608 | 67739.6496
8524-Strainers or filters | 6 | 7 | 635 | 2598.5832
8525-Ducting | 1 | 1 | 395 | 790
8526-Dampers | 5 | 5 | 469.66 | 28696.8571
8527-Other piping; ducting; and damper problems | 6 | 6 | 1114 | 29814.6497
8528-Dry scrubber instruments and controls | 10 | 10 | 1862.9 | 18878.4794
8529-Gas dispersers | 2 | 2 | 142.6 | 2866.1866
8530-Spray towers | 6 | 6 | 534 | 25710.2999
8531-Spray machine/atomizer | 45 | 45 | 4088.85 | 15247.7913
8532-Spray machine/atomizer motors | 4 | 4 | 296.64 | 958.3886
8533-Spray machine/atomizer lubrication systems | 16 | 16 | 1121 | 7950.8329
8534-Spray machine/atomizer vibration problems | 7 | 7 | 309 | 964.2499
8535-Fly ash conveyors | 2 | 2 | 233.39 | 1358.2999
8538-Recycle storage and feed tanks including agitators | 3 | 3 | 617 | 5829.6665
8540-Waste disposal | 2 | 2 | 460 | 3895
8544-Mechanical failures | 14 | 14 | 1457.9 | 14934.5029
8545-Electrical failures | 5 | 5 | 1713.8 | 13733.4763
8547-Inspection | 3 | 3 | 110 | 337
8548-Testing | 1 | 1 | 260 | 338
8549-Other dry scrubber problems | 70 | 70 | 6459.6 | 325300.1938
8550-Electrostatic precipitator fouling | 95 | 98 | 16281.8 | 108765.595
8551-Electrostatic precipitator field out of service | 226 | 226 | 19935.72 | 421157.2622
8560-Electrostatic precipitator problems | 469 | 477 | 52725.63 | 963826.2797
8570-Mechanical precipitator fouling | 2 | 2 | 188 | 1073.8166
8580-Mechanical precipitator problems | 8 | 8 | 732.04 | 3004.1219
8590-Other precipitator problems | 15 | 15 | 1596.41 | 63371.2932
8600-Flue gas additives (furnace injection) | 16 | 16 | 3536 | 70052.0159
8601-SO3 mitigation | 13 | 13 | 2619 | 9899.2823
8620-Mercury Abatement | 3 | 3 | 1344 | 72377.2493
8650-Baghouse systems; general | 431 | 438 | 19145.55 | 466048.5255
8651-Bag failures and rebagging | 488 | 489 | 30351.73 | 935948.4272
8653-Inflation and deflation fans and motors | 3 | 3 | 79.8 | 395.0033
8654-Baghouse booster fans and motors | 16 | 16 | 2876.27 | 35874.2878
8655-Structural duct work and dampers | 39 | 39 | 6104.62 | 51358.8826
8656-Controls and instrumentation B | 81 | 81 | 8887.37 | 89599.5491
8657-Ash handling system and hoppers | 67 | 67 | 7317.8 | 176190.3458
8670-Emission monitors (other than CEMS) A | 11 | 11 | 823.58 | 5875.3312
8699-Other miscellaneous pollution control equipment problems | 74 | 74 | 9313.91 | 57590.1579
8700-CEMS Certification and Recertification | 27 | 27 | 3255.77 | 28807.825
8710-SO2 analyzer problems | 1 | 1 | 313 | 2973.5
8720-NOx analyzer problems | 53 | 53 | 4376.79 | 41147.3295
8730-CO analyzer problems | 16 | 16 | 1643.5 | 10849.046
8740-CO2 analyzer problems | 2 | 2 | 72.1 | 855.5283
8750-O2 analyzer problems | 4 | 4 | 319 | 822.9165
8760-Opacity monitor problems | 17 | 17 | 2357.93 | 16775.3238
8770-Flow monitor problems | 11 | 11 | 979.4 | 5681.6879
8780-Data acquisition system problems | 39 | 39 | 2304.56 | 35395.0866
8790-Miscellaneous CEMS problems | 157 | 158 | 12218.81 | 103644.7928
8800-SNCR NOx Reagent | 3 | 3 | 30 | 208.7667
8802-SNCR NOx Control system | 13 | 13 | 995 | 22000.8497
8809-Other SNCR NOx problems | 28 | 33 | 1970.79 | 42770.3217
8810-SCR NOx Reactor | 1 | 1 | 67 | 139.5833
8812-SCR NOxCatalyst | 44 | 46 | 1416.27 | 102697.9457
8813-SCR NOx Injection grid piping/valves | 23 | 23 | 1843.36 | 16384.6556
8814-SCR NOx Catalyst support material | 2 | 2 | 100 | 54.1666
8815-SCR NOx Soot blowers | 2 | 2 | 114.8 | 406.5833
8816-SCR NOx Plugging | 29 | 29 | 1169.04 | 52080.6602
8817-SCR NOx Control system | 49 | 53 | 2989.59 | 21427.6604
8820-SCR NOx Ammonia injection grid piping/valves | 90 | 90 | 8286.31 | 60694.673
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 22 | 22 | 1665.4 | 7602.6228
8822-SCR NOx Ammonia air blowers | 35 | 35 | 2474.12 | 20248.1274
8823-SCR NOx Other ammonia system problems | 125 | 127 | 9106.18 | 156375.3542
8825-Other SCR NOx problems | 85 | 86 | 7886.42 | 174153.8253
8835-CAH NOx Other CAH problems | 4 | 4 | 196 | 1551.6666
8840-CO Active catalyst | 27 | 46 | 2179.9 | 6067.551
8841-CO Support materials | 2 | 2 | 196.2 | 238.71
8842-CO Plugging | 7 | 7 | 67.4 | 980.8666
8845-Other CO reduction problems | 55 | 55 | 2906.05 | 71231.861
9000-Flood | 158 | 159 | 7707.37 | 5357597.9117
9010-Fire; not related to a specific component | 9 | 9 | 928.15 | 512432.7004
9020-Lightning | 234 | 236 | 35294.37 | 3023751.8257
9030-Earthquake | 5 | 5 | 1217 | 356925.5498
9031-Tornado | 2 | 2 | 94.8 | 14403.28
9035-Hurricane | 15 | 15 | 2971.13 | 284736.3404
9036-Storms (ice; snow; etc) | 66 | 66 | 5881.49 | 105234.7513
9040-Other catastrophe | 28 | 29 | 3193.81 | 942871.9854
9110-Core coastdown (nuclear) | 7 | 7 | 2786.61 | 854143.5897
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 401 | 461 | 35298.24 | 1562197.1807
9131-Lack of fuel: Contract or Tariff allows for interruption | 611 | 669 | 37157.3 | 1732444.8225
9132-Wet Fuel - Biomass | 148 | 166 | 1256.44 | 19878.1539
9134-Fuel conservation | 218 | 218 | 14663.67 | 317909.175
9135-Lack of water (hydro) | 2378 | 2616 | 33408.55 | 1224435.9608
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 19 | 19 | 1368.8 | 163374.7729
9137-Ground water or other water supply problems | 32 | 32 | 3380.87 | 163379.36
9160-Other economic problems | 20 | 20 | 3845.65 | 56972.5496
9180-Economic (for internal use at plants only) | 2 | 2 | 112 | 695.8666
9181-Economic (for internal use at plants only) | 23 | 23 | 10984.48 | 27780.3281
9182-Economic (for internal use at plants only) | 90 | 90 | 27345.18 | 106672.4625
9184-Economic (for internal use at plants only) | 10 | 10 | 614.2 | 26191.3854
9200-High ash content | 526 | 655 | 50848.64 | 535372.7828
9201-High ash content ? (not outside management control) | 5 | 5 | 175.3 | 7804.515
9205-Poor quality natural gas fuel; low heat content | 6 | 6 | 464.82 | 2491.2723
9210-Low grindability | 4 | 4 | 123.32 | 282.4126
9211-Low grindability (not outside management control) | 1 | 1 | 18 | 156.9
9220-High sulfur content | 48 | 62 | 6629.83 | 21914.517
9221-High sulfur content ? (not outside management control) | 1 | 1 | 4 | 156.8667
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 685 | 689 | 30044.96 | 1058676.2787
9251-Low Btu Coal From Contract For Low Btu Coal | 61 | 61 | 1256.53 | 40435.4255
9261-Low Btu oil (not outside management control) | 1 | 1 | 16 | 374.4
9270-Wet coal | 1069 | 1078 | 102882.63 | 1023441.1267
9271-Wet coal (not outside management control) | 327 | 328 | 35303.99 | 491872.2595
9272-Wet Fuel (other than coal) | 1 | 1 | 102.5 | 155.4583
9280-Frozen coal | 9 | 9 | 375 | 3019.5832
9281-Frozen coal (not outside management control) | 20 | 20 | 2793.8 | 12517.5245
9290-Other fuel quality problems | 243 | 255 | 16130.92 | 302366.9726
9291-Other fuel quality problems (not outside management control) | 253 | 255 | 6924.58 | 103586.8939
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 1211 | 1218 | 92613.14 | 2396245.6126
9305-Ash disposal problem | 8 | 8 | 913.53 | 28866.1332
9310-Operator training | 1 | 1 | 27.66 | 82759.181
9320-Other miscellaneous external problems | 1021 | 1269 | 43753.63 | 2265170.7877
9340-Synchronous Condenser Operation | 1 | 1 | 61.6 | 452.76
9345-Pumping Operations | 2 | 2 | 196 | 166.5999
9350-Public Safety/River Rescue | 27 | 30 | 261 | 3436.4999
9504-Regulatory (environmental) proceedings and hearings - regulatory agency initiated | 1 | 1 | 24 | 50470.4
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 16 | 16 | 3761 | 303357.9126
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 102 | 106 | 1265.73 | 122616.984
9600-SO2 stack emissions (fossil) | 52 | 53 | 6659.77 | 101237.4905
9610-NOx stack emissions (fossil) | 171 | 177 | 5778.18 | 156749.1356
9613-NOx stack emissions (gas turbine) | 144 | 147 | 12334.51 | 251541.5232
9614-NOx stack emissions (jet engines) | 40 | 40 | 1577.64 | 9758.1002
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 4 | 4 | 23.57 | 1098.2142
9616-CO stack emissions | 101 | 114 | 6257.34 | 181881.1738
9620-Particulate stack emissions (fossil) | 84 | 85 | 7643.57 | 418148.0736
9630-Opacity (fossil) | 487 | 488 | 42124.17 | 782088.0174
9633-Opacity (gas turbine) | 2 | 2 | 98 | 2227.05
9634-Opacity (jet engines) | 1 | 1 | 46.9 | 16.415
9650-Other stack or exhaust emissions (fossil) | 103 | 105 | 9466.73 | 143684.3419
9653-Other stack or exhaust emissions (gas turbine) | 16 | 16 | 3435.37 | 37888.1627
9654-Other stack or exhaust emissions (jet engines) | 9 | 9 | 434.3 | 467.8883
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 1 | 1 | 9.04 | 354.5187
9656-Other stack or exhaust emissions testing - fossil | 34 | 34 | 3290.79 | 40667.2413
9657-Other stack or exhaust emissions testing - gas turbine | 11 | 11 | 455 | 10102.9332
9658-Other stack or exhaust emissions testing - jet engines | 4 | 4 | 64.8 | 529.5733
9660-Thermal discharge limits (fossil and nuclear) | 126 | 126 | 11598.98 | 186208.325
9663-Thermal discharge limits (gas turbine) | 5 | 5 | 138 | 32437.1666
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 191 | 201 | 8550.31 | 166552.743
9693-Other miscellaneous operational environmental limits (gas turbines) | 41 | 41 | 4609.39 | 280607.1309
9694-Other miscellaneous operational environmental limits (jet engines) | 21 | 21 | 722.18 | 9912.6543
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 2 | 2 | 5.14 | 771.6853
9696-Other miscellaneous operational environmental limits (hydro and PS) | 29 | 29 | 635.77 | 61807.9417
9720-Other safety problems | 29 | 29 | 2669.64 | 1078530.3791
9900-Operator error | 533 | 535 | 117961.62 | 1448057.3767
9910-Maintenance personnel error | 185 | 185 | 32683.91 | 304371.5821
9920-Contractor error | 79 | 79 | 16399.09 | 701837.7341
9930-Operating procedure error | 65 | 65 | 14539.89 | 497289.0381
9940-Maintenance procdure error | 26 | 26 | 3377.37 | 67857.0302
9950-Contractor procedure error | 10 | 10 | 1648.66 | 188723.4016
9960-Staff shortage | 6 | 6 | 1075 | 5552.65
9997-NERC Reliability Standards requirements | 15 | 15 | 2058.52 | 60233.1128
9998-Black Start testing | 9 | 9 | 743.26 | 733.6005
9999-Total unit performance testing (use appropriate codes for individual component testing) | 191 | 204 | 5173.13 | 2190855.1948
Total Result | 70600 | 72952 | 8386191.7 | 352268861.0482

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 768.3665 | 178 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 740.3199 | 158.64 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1492.8332 | 265 | 2 | 2 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 821.4999 | 318 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 34.2333 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 39 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 78 | 39 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 20.8 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 84.5 | 39 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 196 | 20 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 13 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 26 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 48.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 55.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 549.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 84.5 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 263.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 15.6 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 32.5 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 195 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 9.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 37.9167 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 78 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 156 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 54 | 18 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 40 | 20 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 32.5 | 26 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 35.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 52 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 40.95 | 21 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 57.35 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224.1667 | 5 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 30.7667 | 26 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 70.6333 | 26 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 144.6666 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 167.9166 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 72.3333 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 981.3333 | 8 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 7.3333 | 11 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 627.5 | 50 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 584.325 | 220.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 351.9 | 153 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.875 | 220.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.0499 | 159 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 801.35 | 141 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1543.0666 | 142 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26.6666 | 80 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 483.3333 | 145 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1737.6666 | 130 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.45 | 73 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 238.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 668.6666 | 59 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1126.5998 | 258 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1539 | 405 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.8933 | 74.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.5 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 290.7666 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 400 | 120 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 806.6666 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2631.2497 | 375 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7420.8332 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1144 | 208 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5620.2999 | 186 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10251.4666 | 148 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 1.4 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 158.7 | 46 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3897 | 433 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6723.5999 | 234 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.5 | 267 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 316.8 | 288 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2162.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5169.75 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11658 | 134 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 504 | 63 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 510 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 904.3998 | 228 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1071.4666 | 224 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1141.1833 | 229 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1347.5166 | 233 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.5667 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1540 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3565 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 189.4182 | 391.9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1905.7498 | 297 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2556.1326 | 256.04 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 41.3333 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 354.2499 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1594.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3775.6665 | 470 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11747.5 | 635 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10855 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 3216.4 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.9 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148.8666 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 159.0667 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1558 | 410 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16582.5 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.65 | 23.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 400 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 410.6666 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13262.6665 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 138.8333 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 425.3333 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1078 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1180.3 | 319 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1785 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4394.25 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3369.4365 | 276.94 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2396.8332 | 197 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 32 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 104 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 139.3333 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 715 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1395.3332 | 161 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3578.6665 | 440 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 495 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 3 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.6667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.5 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.6666 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1671.345 | 257.13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3266.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.5833 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.5666 | 77 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 536.6666 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 893.3333 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1443.0666 | 79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0.7 | 0.6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.8583 | 29.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192.9 | 3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 459.1666 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 891.6 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3024 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7360 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3536 | 442 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.6666 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 764.05 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 770.9333 | 112 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12513.6665 | 310 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 357.6666 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3090.7332 | 259 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2856.5 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3123.75 | 425 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3567.4164 | 445 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4965.0999 | 246 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3744.9 | 342 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38398.3079 | 159.12 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 117.3331 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 340 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4578.6666 | 136 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 347.2831 | 311 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 467.2832 | 529 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 533.8666 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1190 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1213.3332 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1380.5 | 251 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2295.1665 | 235 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4925.6 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5265 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.49 | 18.83 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 63 | 63 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 72 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.6833 | 11.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 240.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 517.4998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1326.75 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1466.8333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1592.5 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1661.8333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1993.3333 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2881.6665 | 380 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 334.048 | 140.16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 22 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2916.9332 | 334 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5520 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1366.083 | 485 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10785.5999 | 189 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7074.2 | 434 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 845.75 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 385.3333 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1263.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3232.1665 | 473 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.45 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320.8333 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 542.5 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 584 | 146 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 587.5 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1224.0665 | 244 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6665 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7471 | 241 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.9998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3340.5 | 255 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.0266 | 108.16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6793.7497 | 375 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 157.3333 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 13.3333 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.4166 | 77 | 1 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.1333 | 136 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28137.2665 | 374 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 10.4367 | 20.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 76.2 | 38.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1094.5 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2377.5832 | 277 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82 | 41 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.6666 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 130.6548 | 15.71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.1 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1255.9832 | 179 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1590 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4777.5 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5305.1665 | 458 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7830 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.3332 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75.9332 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 204.2498 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 641.3333 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1941.1665 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 99.2 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 312.8 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.5 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.9 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9758.6666 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1544.7 | 114 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.95 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134.7333 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2166.2666 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 222 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.5999 | 144 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1296.9666 | 82 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1483.0832 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4499.133 | 434 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1208.85 | 241.77 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 618.4 | 123.68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1506 | 251 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 120.75 | 13.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 566.8 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2703 | 340 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1300 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1499.7332 | 304 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2570.7499 | 339 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1694.3332 | 460 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 842.0833 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 13.9533 | 18.2 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 94.4533 | 35.2 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 1603.0999 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 1476.6 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 19 | 15.2 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4053.06 | 184.23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 37.5 | 12.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 84.99 | 28.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 138.3333 | 33.2 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 151.5 | 20.2 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 265.9999 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 308.8332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 376.6 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 206.5 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 409.0666 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 45.3333 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 770.25 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 172 | 80 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 90.8332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 85.5833 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 87.8333 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 58.9666 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 12046.25 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 279.9999 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 91.6663 | 550 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 86.5333 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 71.4 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 74.75 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 222.6499 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500.5075 | 105.37 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 526.2949 | 82.02 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 576 | 4 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1439.8 | 12 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 755 | 5 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1320 | 11 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1234.9167 | 5 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 134.5833 | 25 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.5 | 7 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1778.6666 | 230 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3344.0666 | 206 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253.3333 | 38 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314 | 60 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4796.25 | 75 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 437 | 60 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3992.7332 | 271 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134694 | 280 | 1 | 1 | 0050-Coal storage fires | U1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 611.1667 | 38 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1535.0998 | 306 | 1 | 1 | 0050-Coal storage fires | U1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.7166 | 73 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.7666 | 122 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.5666 | 119 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.5 | 58 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.5999 | 78 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.6 | 91 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 390 | 130 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5499 | 81 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 72 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52 | 104 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141 | 188 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 95 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.3333 | 92 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.2 | 84 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.55 | 117 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 399 | 133 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 5.4667 | 8 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1061.0664 | 346 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.8 | 84 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6 | 84 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.4 | 108 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1777.7665 | 401 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.4 | 108 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6833 | 31 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.8333 | 113 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1.25 | 5 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.65 | 87 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.4666 | 74 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.1666 | 85 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.3999 | 108 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.6166 | 89 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 109.43 | 35.3 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 110.4 | 27.6 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32106.25 | 25 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41 | 5 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.9 | 153 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329 | 47 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 432 | 216 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3718 | 26 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.25 | 15 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.8664 | 388 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 801 | 89 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 880 | 110 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 540 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4194.8665 | 202 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.3333 | 220 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 672 | 32 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 50 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 90 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 91.6665 | 500 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.75 | 95 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 256.6666 | 154 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.1666 | 85 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.5 | 15 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 182.85 | 23 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 677916 | 270 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3.8 | 3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 100.7 | 19 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 195.2 | 18.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 299.7 | 33.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 375.6 | 31.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 140.85 | 31.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 117.505 | 21.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 749.8 | 16.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 249.85 | 26.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 412.695 | 24.3 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1845.3331 | 320 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.8333 | 70 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1556.9998 | 270 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 17.7833 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 58.4667 | 8.77 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 562.4999 | 270 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1252.8999 | 224.4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 15.2167 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 434.35 | 51 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2015.5833 | 19 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 1380 | 4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.1 | 54 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 216.5833 | 23 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 35.5667 | 11 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.6 | 33 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.0333 | 53 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.8166 | 43 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 550.2 | 63 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2274.95 | 263 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1534.35 | 53 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 414.75 | 63 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 892.5 | 525 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | U1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 478.54 | 21.3 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 800-Miscellaneous
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.3333 | 118 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.0666 | 28 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.2667 | 14 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1405.04 | 150.54 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171.5466 | 73.52 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1433.3333 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 96.4333 | 11 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2379.75 | 285 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1950 | 50 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260.6666 | 85 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200010 | 590 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 670.0832 | 215 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4818.3331 | 350 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2482.2695 | 257.23 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 416.6666 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 604.3332 | 245 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 252 | 36 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 800-Miscellaneous
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 4858.8 | 36 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.2333 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5333 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.316 | 7.44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.4999 | 90 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.6666 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.04 | 13.84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 141.1666 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 167.1666 | 118 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 180.6 | 63 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.1497 | 25.82 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 24.805 | 12.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 198 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.6 | 85.4 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.8 | 94 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 227.3667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.9333 | 107 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66.6666 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.1666 | 95 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 75 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 21 | 7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 480 | 40 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 96.03 | 58.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 244.4 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325.8755 | 29.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378.3833 | 73 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 386.4966 | 24.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1082.8333 | 73 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.3333 | 10 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.3 | 69 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.6 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.1666 | 94 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 971.6666 | 106 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52 | 48 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.1667 | 10 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.6499 | 111 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1232.5 | 85 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 253.8 | 81 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 33 | 11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 313.5 | 38 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1431.4164 | 445 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.3333 | 86 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.9666 | 94 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.02 | 6.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.0833 | 41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 246.99 | 82.33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.56 | 11.64 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 906.6666 | 85 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1346.4 | 10.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 836 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 128 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 192 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 24 | 3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 603 | 67 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.6833 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8333 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.8 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.6666 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 452.01 | 150.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.1153 | 5.08 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 321.7333 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 487.5 | 45 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 896.7 | 61 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 380 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 14 | 2 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 54 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.4667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.1872 | 23.41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.2 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 847.5 | 113 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.6666 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392.7333 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 30 | 10 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 600 | 150 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15843.6328 | 842 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1623.5 | 51 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.5 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.5 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.75 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.85 | 113 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45.5 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.5 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 518.75 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 763.3212 | 11.93 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1300.8666 | 79 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 24.2833 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 120 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 192 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.3333 | 8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.334 | 136.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.7333 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 808.2999 | 177 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57 | 95 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.6677 | 6.37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164 | 16.4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 291.6665 | 250 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 384.8 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1147 | 124 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 379.4166 | 145 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 141.9 | 11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 135 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 273 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.9 | 76.9 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 57.6333 | 1.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 65.675 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 655.2 | 27.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 52.6 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 145.55 | 12.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 37.6667 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 117.15 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 158.1 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 22.6 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 101.525 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 35.9667 | 8.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 233 | 23.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 135.8833 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 57.05 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 333.8666 | 31.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 16.8 | 6.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 20.475 | 6.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 26.675 | 3.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 82.225 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 431.05 | 23.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 191.525 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 92.3 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 115.375 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 315.875 | 13.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 64.575 | 6.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2.995 | 0.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 34.425 | 15.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 384.0117 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 105.2 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39.525 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 42.63 | 6.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 75.075 | 27.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 464.6666 | 82 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 163.2258 | 150.67 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1710 | 45 | 1 | 1 | 0100-Bunker gates | D3-Forced - Postponed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77.8461 | 150.67 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 840 | 45 | 1 | 1 | 0100-Bunker gates | D3-Forced - Postponed | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450.2167 | 7 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1481.48 | 9.24 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1744.0227 | 8.17 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 7.65 | 2.25 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 5.8333 | 14 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 24.2666 | 28 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 48.3333 | 29 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 615.5671 | 128.69 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 167.75 | 61 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4019.1665 | 265 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.3333 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 184.25 | 55 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13021.6666 | 130 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1854.2186 | 158.03 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 212.5 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2418 | 372 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2782.5 | 265 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.9 | 22 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.933 | 72.57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.3128 | 70.21 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2682.7665 | 533 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 174 | 58 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.5 | 294 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 760 | 190 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2859.9999 | 264 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11191.6666 | 170 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.9 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440.8333 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2181.828 | 165.29 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1670.4 | 348 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2268 | 420 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.3333 | 145 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 294 | 392 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 380.8 | 224 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 783.5333 | 46 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3444.0444 | 201.21 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5220.5 | 394 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.5 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 715 | 130 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.47 | 37.14 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2249.9999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.346 | 56.22 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6742.4 | 301 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.6 | 76 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.5 | 130 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.3333 | 125 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.0584 | 86.31 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315.8666 | 46 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2346.7525 | 273.94 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5033.8666 | 344 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12045.5999 | 432 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.7133 | 31.12 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2595.8333 | 178 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 200 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 427.5 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2650 | 265 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.782 | 84.28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3440 | 160 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4413.4998 | 291 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 286.1666 | 170 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.446 | 8.76 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 191.3333 | 82 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 639.9998 | 240 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132 | 132 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2015 | 310 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84 | 84 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5150.7165 | 371 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284.6666 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 344 | 172 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.2 | 46 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 711 | 316 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.1666 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 108 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6666 | 76 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3109.7333 | 83 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 421 | 421 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5565 | 420 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 738 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9468.3332 | 260 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 45 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3409.733 | 428 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 6639.033 | 518 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 12168.8667 | 38 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 400.96 | 50.12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 700.02 | 116.67 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21 | 10.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 116.6 | 33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 121.5667 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 705 | 35.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 31.35 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 140.6833 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5.4667 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 84.6 | 28.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 6.2 | 6.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 116.8 | 29.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3.15 | 4.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.2 | 4.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1111.5 | 190 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 540 | 67.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 997.08 | 47.48 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 161.5 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 261.99 | 87.33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 365.2 | 33.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 54.99 | 18.33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 631.95 | 42.13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.55 | 3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 77 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 306 | 102 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 15.03 | 5.01 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5.2 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.6 | 11.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1146 | 114.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2579.04 | 107.46 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 329 | 82.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 470.03 | 42.73 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 11.8333 | 14.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 76.9133 | 33.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 158.8533 | 32.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 5.2 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 30.4 | 15.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 171 | 34.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 137.8666 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.8 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2 | 3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 20.3333 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 120 | 60 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 4.96 | 6.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 21.93 | 10.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2.2 | 2.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.3733 | 6.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 239.4 | 34.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 224 | 224 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 154.02 | 25.67 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 18.87 | 6.29 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1.6 | 3.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5366.7831 | 293 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 50 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 720 | 45 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 13.95 | 9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 21.0833 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 729.98 | 38.42 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 832 | 83.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 49.14 | 16.38 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2.46 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10.5 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 184.02 | 30.67 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 31.5333 | 43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 40.8 | 27.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 9.2 | 9.2 | 1 | 2 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 65.1 | 25.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 9.5 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.6667 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 30.15 | 27 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 46.55 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 158.3333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 22.6667 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 72.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 167.65 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 41.25 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 104.165 | 12.55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | WECC | Winter | 101.2667 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 33.3333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Summer | 284.9 | 66 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 10.15 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 38.75 | 25 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 117.9167 | 25 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 53.9 | 4.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.4 | 10.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 43.38 | 14.46 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 267.4 | 28 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 4.25 | 3 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 68.5417 | 12.5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 813.3333 | 61 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 31.5 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.58333 | 1 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 6.1667 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.5333 | 8 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1.3 | 2 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 36.3 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3.3 | 6 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 44 | 33 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 83.5 | 30 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 14.0833 | 13 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 77.1 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 352 | 70.4 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 246 | 123 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 39 | 39 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 39.99 | 13.33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 49 | 49 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.34 | 3.34 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 19.44 | 9.72 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 4.66 | 2.33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 45 | 7.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 48.58 | 24.29 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 83.98 | 41.99 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 259 | 37 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 9.26 | 4.63 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 250 | 12.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 54 | 18 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 84 | 21 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 726.96 | 90.87 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 11 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 16 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 70 | 35 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 83 | 16.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 12.16 | 6.08 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 9.14 | 9.14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 10.84 | 5.42 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 85.3833 | 54.5 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 253.2 | 36 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 37.03 | 5.29 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 55 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 65 | 32.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 620.96 | 77.62 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 32 | 32 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 266.98 | 38.14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 511.02 | 85.17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1008 | 144 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 14 | 14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 41.92 | 20.96 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 11.66 | 5.83 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 66.4 | 33.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 119.875 | 41.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 20 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 235.98 | 39.33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3528 | 117.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 7.44 | 3.72 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 16.5 | 8.25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 4.09 | 4.09 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 8.03 | 8.03 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 15 | 15 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 26 | 26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 53.34 | 17.78 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 44.5083 | 54.5 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 39 | 39 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 134 | 26.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 69 | 34.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.26 | 2.26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.44 | 2.44 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 10.12 | 5.06 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 97.3375 | 9.75 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Oil | OL | 800 | Miscellaneous | NPCC | Off-Peak | 172.55 | 17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 18 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Summer | 67.76 | 23.1 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Winter | 6.6667 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 320.9999 | 90 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 10 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.352 | 120.66 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490.8333 | 38 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640.3 | 38 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 810.6667 | 38 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 868.6999 | 219 | 2 | 2 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.3333 | 220 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.7467 | 14.9 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 39932 | 596 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 4 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.9833 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 330.4167 | 13 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3520 | 320 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4202 | 382 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.6667 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 8 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 50 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.3 | 21 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 959 | 30 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 41461.7329 | 596 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.8167 | 11 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.8333 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 594.75 | 61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2818.3333 | 178 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 12.6 | 21 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136 | 8 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.1667 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 1 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 719 | 179.75 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9833 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 3 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.5 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 6 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1204.5 | 146 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 374.7917 | 12.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 37.5 | 12.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 150 | 12.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 601.7499 | 87 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 33 | 33 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 60 | 16 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 585 | 32.5 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 314.25 | 419 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 365.3332 | 274 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 116.7999 | 219 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 363.1331 | 419 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 327.5332 | 289 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 67.7333 | 127 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 310.206 | 37.83 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0134 | Sorbent handling crushers | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 169 | 33.8 | 1 | 1 | 0134-Sorbent handling crushers | D1-Forced - Immediate | 650-Fluidized Bed
0134 | Sorbent handling crushers | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 24 | 24 | 1 | 1 | 0134-Sorbent handling crushers | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 243.3333 | 50 | 1 | 1 | 0160-Bed material tanks/hoppers | U1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 208.5 | 30 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0170 | Bed material cyclone | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 180.05 | 39 | 1 | 1 | 0170-Bed material cyclone | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 47.46 | 23.73 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 35.425 | 54.5 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 100.89 | 11.21 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1450.8 | 108 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 53.5916 | 54.5 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.6667 | 4 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5512 | 65 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 514.8 | 72 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 64 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151 | 151 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 30 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3666.6666 | 80 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1760 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85 | 85 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103 | 103 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.5 | 82 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1182 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 919.6 | 57 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3469.6667 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 78 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 5 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.6666 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3572.7499 | 93 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.5 | 54 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 686.6666 | 80 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 78 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 426 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 653.1333 | 97 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 84 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1293.2825 | 14.33 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12943.3333 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 110 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.5 | 30 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1692.6167 | 41 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 60 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D3-Forced - Postponed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 337.1666 | 119 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1992 | 40 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.9999 | 240 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D3-Forced - Postponed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 57.2411 | 118.43 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.4 | 119 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96 | 16 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54816.1166 | 37 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.2333 | 53 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1026.2666 | 43 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1764 | 80 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1560 | 144 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.9332 | 286 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129.5 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190.6666 | 65 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 187.9165 | 205 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 336.2666 | 194 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35 | 105 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.9999 | 360 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.9666 | 338 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 348.8333 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 362.95 | 119 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 439.1666 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 481.6666 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2245.4998 | 270 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.8333 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 120 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.5832 | 265 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400 | 320 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 498.6664 | 680 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 662.9999 | 180 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 285 | 300 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2000 | 125 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.5 | 102 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1107.2 | 128 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1879.5 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9408 | 392 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186 | 124 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 930 | 124 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.0666 | 124 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100.8333 | 110 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3564.3332 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.3333 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.6666 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 114 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.5 | 109 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.6666 | 40 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.5 | 15 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.3332 | 140 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 449.9999 | 108 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9272 | 96 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 226.05 | 137 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 444.15 | 63 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.1666 | 95 | 1 | 6 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.75 | 95 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.5333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.0833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.5499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.2166 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.217 | 118.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.0833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.3 | 54.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132.5 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.4666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168.1333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.9 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.9833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 197.7082 | 162.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.025 | 67.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.1166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290.6833 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 325.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 382.7 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 476.9333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 569.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 576 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 578 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 591.6666 | 284 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620 | 248 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 636.5666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 731.4998 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 816.3332 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 848.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1052.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1178.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1776.8519 | 166.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2411.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2437.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2521.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2522.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3567.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3641.6665 | 287.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4185 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6455.3332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 2 | 3 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1667 | 10 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.3667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.7 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.4 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.9 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.3 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.2833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.2333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.0999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.5 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.8833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.4 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.7333 | 76 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.4 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.25 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.0166 | 291.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.0665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 194.67 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222.0166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.4999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 252.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 406.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 489.0599 | 118.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 585 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 593.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 678.6499 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 744.1666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 786.6833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 880.4 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1028.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1256 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1276.9333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.2 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.5832 | 295 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.89 | 80.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 47 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 71.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.8333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.1166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.439 | 91.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 184.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 190.4761 | 57.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.3333 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.9 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 263.22 | 87.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 296.45 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 325.5 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 336 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 337.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 385.7 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 408 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 504.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 553.6666 | 302 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 580 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 594.3 | 84.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 882 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1074.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1132.4333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1228.2997 | 519 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2276.3 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3393.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4924.8167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.35 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.7 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 189.1913 | 79.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1314 | 262.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.3899 | 102.15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 300 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 469.7833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2105.85 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.74 | 4.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.2133 | 30.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.2 | 23.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 230.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 236.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 236.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 317.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 549.9 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 748.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.8 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.15 | 91 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 170 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 253.1666 | 245 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.2667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.8333 | 175 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 529.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315.2499 | 195 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 662.833 | 485 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1268.7496 | 525 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 510 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2108.7497 | 525 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300.31 | 101.8 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 723.102 | 190.29 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1.1 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5833 | 95 | 1 | 5 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.6 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.2665 | 458 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.79 | 28.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 30.1933 | 90.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.8333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.0553 | 117.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.3333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.7 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 78.9466 | 76.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81.7646 | 100.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.8333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 124.074 | 68.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.2 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.5 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 221.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.1333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 239.4166 | 221 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 261.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 322 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 414.5166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.0476 | 276.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 530.764 | 61.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 570 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 579.6666 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 609.7499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 626.4 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 628 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 645.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 737.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 961.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1134.9333 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1732.5332 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2006 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2246.0499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3061.6833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3207.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3514.9998 | 277.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4746 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5548.8333 | 169 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.4666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.9833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.3333 | 10 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.3333 | 95 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.0333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.95 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.9 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 37.3575 | 149.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.85 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.0333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.7999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.6 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.6666 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57 | 95 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.2 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.6333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.15 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.7833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.6833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.1331 | 308 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.4 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 124.5733 | 93.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132.9162 | 306.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.75 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.9981 | 332.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175.8875 | 140.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176.25 | 23.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 201.0393 | 70.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232.8 | 38.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 241 | 60.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 277.9166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.3609 | 106.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360.25 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 415.1666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 425 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725.0833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 750.5333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 766.3 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 777.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 795 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 814.2666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855.8999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1018.3333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1023.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1078.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1193.7999 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1475 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.2 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.95 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.25 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.6833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.45 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.65 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.9666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30.8 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.9166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.4166 | 92.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.5565 | 146.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.05 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.4666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.3 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.3333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.7499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.45 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 67.0999 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.5 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.9333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 112.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 118.972 | 84.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140.4 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 166.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 172.125 | 67.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 197.8 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 273 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 277.3333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 282.3333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.9998 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 450 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 503.75 | 325 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 542.5 | 217 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 595 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 631.3666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 670.4999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 740.2666 | 347 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1068 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1315.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1731.2332 | 334 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1909.6 | 35.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2160 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3618.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6778 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29245.6666 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.1667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 357.5732 | 202.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.1666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31.2 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.5 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 97.1666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 207.8333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 224.6833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 289.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 762.85 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 881.5 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345 | 69 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 584.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1033.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.8133 | 21.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.12 | 27.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.1 | 26.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 834.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.2999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 641.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 777.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 290.1333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 482.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 788.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 799.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 971.6665 | 233.2 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6260.8995 | 822 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 352.8981 | 384.98 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4071.6662 | 700 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Off-Peak | 91.7999 | 162 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6.0683 | 36.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.0333 | 54.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.4 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 23.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.7333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.5999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.8 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.1333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.9 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116 | 232 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132.1666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.1999 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.0998 | 309 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 229.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 261.87 | 49.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.5832 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 329.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.888 | 104.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.4896 | 90.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355.683 | 134.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 369.75 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 444.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 552.9333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 573.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 581.4 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 592.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 617.5 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 631.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 721.5 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 863.3332 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1079.6666 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1207.4999 | 207 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1279.2 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1678.1166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1980 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2171 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2662 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3661.35 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3673.3331 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8051.25 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.99996 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.65 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.4 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.0853 | 60.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.2667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.0167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.2 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.8 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.0666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 44.7766 | 141.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.405 | 20.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.6 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.8667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.7666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.4833 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.25 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 152.8623 | 60.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.3999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.9333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 188.8133 | 23.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206.8 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207.9 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239.9833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 346.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 368.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 487.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 612.25 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 709.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 710.6666 | 164 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 742.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 792.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 840 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 950.95 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1380 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1500 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1683.3333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1899.645 | 131.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1980 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2312.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2440 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2767.5 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5798.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.66666 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.4 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.4167 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.25 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.455 | 95.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.9999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.4333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.9999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115.2 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 115.375 | 32.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.1333 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.9333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.4999 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 241.9999 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 264.0664 | 466 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 422.8 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 553.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 647.7999 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 928.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 976.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1029 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1301.75 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5303.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.1666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.3333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 243.2667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 300 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 738.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 760.05 | 112.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1808.3333 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.5666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.8833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 256.9333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 322.4 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 551.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1320.55 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.9 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 535.2666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2673 | 148.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.25 | 57 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.1 | 1.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 314.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.7 | 7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.125 | 37.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.8 | 6.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3532.8332 | 517 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.1721 | 54.23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96.8 | 44 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 262.4165 | 235 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 671.2499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 760.5 | 117 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 828.9166 | 245 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 979.7975 | 97.17 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.8666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 246.4 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 264.5833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 948.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.7359 | 130.08 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7183.2 | 876 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1113.4165 | 431 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2554.9999 | 420 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 3 | 6 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 18.3733 | 42.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.2 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.4333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.4 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.3166 | 73 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.15 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.4333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.9006 | 100.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.15 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 195 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.7666 | 203 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.064 | 108.09 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 411.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.7333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 487.3499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 584.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620.6665 | 380 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 979.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1004.2666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1109.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1180 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1374.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2827.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3422.9165 | 265 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.55 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.45 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.0833 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.0333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 13.615 | 38.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.5 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.75 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.0833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.65 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.1667 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.283 | 55.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.0893 | 30.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.2 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.6333 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.7833 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 138.0533 | 66.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.4999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 167.2665 | 193 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 174.1071 | 103.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.1333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.75 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 299.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 315 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 390.8666 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 425 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 645.75 | 287 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 654.5 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 849.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1200.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1282.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1385.695 | 111.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1419.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1957 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2015.5333 | 196 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2976.4165 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4658.4999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.3 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.5 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.1333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.33 | 61.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.4333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.225 | 25.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.0666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.3332 | 218 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 64.75 | 259 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.8 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.335 | 136.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.3333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136.2666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 169.75 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.5 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 272.8 | 248 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288.15 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 367.9432 | 242.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 373.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 419.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 457.8333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 534.75 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 674.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 694.4 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 710.5999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 756.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 767 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 849.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 937.4665 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1096.5332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1474 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2260.5 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3168 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4153.0831 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6921.5 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.15 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.0333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.4666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.7 | 91.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.8 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 157.7 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.4006 | 96.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 249.1333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 329.8 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 659.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 664.8 | 332.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 284 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 479.49 | 159.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 914.4 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.4 | 9.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143.3333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 307.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.8666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.095 | 14.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 247.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 407.8666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.4333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.3166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 920.9166 | 215 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 606.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1392.1333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1580.25 | 215 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.71 | 53.57 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 31 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 799.9995 | 750 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 945.9998 | 330 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.95 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.931 | 59.31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.856 | 27.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.15 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.2 | 242 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.6667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.65 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.998 | 108.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.1 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.35 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.2 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.0666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.0666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.6 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.3332 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.5999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 298.1333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 363.15 | 134.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 367.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 384 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 413.7166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 427.7 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 464.3999 | 324 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 517.1666 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 577.5 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 579.6666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 587.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 730.38 | 25.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 742.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 879.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 903.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1015.4333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1539.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1848 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3536.9999 | 405 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3972.2666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5870.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.1 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.6666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.55 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 35.5416 | 85.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.7 | 102 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.1666 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.9 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68 | 68 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.9035 | 61.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.1166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 155.7166 | 93.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170.8333 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189.9999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.5525 | 48.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 222.8332 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 232.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.7 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270.6666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.8666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 378.7333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 402.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 402.8683 | 130.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 437 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 507.3 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 520 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 529.1 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 587.1999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 604.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 622.5832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.25 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 733.6666 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 813.7 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 867.9067 | 23.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 883.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 892.4 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 892.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 945.8166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1134.7666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1139.8053 | 68.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1215.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1471.2666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1738 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2443.9999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2690.8 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3396.3733 | 108.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 2 | 10 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.2667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.4667 | 18.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.2667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.2733 | 52.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.4 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.4142 | 24.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.7 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25.25 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 34.1666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.2 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.9333 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.6665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.1 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.4 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.4666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.1333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119.4666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 127.05 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 141.1666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196 | 196 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 204.9999 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310.3332 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 337.7703 | 67.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 407.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 410.4665 | 262 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 421.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.7498 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 534.8325 | 73.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 566.6666 | 272 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 576 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1138.7333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2879.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.7 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.9 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.9 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 287.9691 | 58.57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 342 | 342 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 479.0132 | 202.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 510 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 620.15 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.2 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 111.3 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 18 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.1166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.8 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 130.3333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 666.9333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1178 | 117.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.9 | 29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4506.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1104 | 46 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.5783 | 11.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17 | 17 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.5 | 109 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 950.4 | 13.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.6999 | 273 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 115.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 709.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.4 | 52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 235.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 320.85 | 69 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 444.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 474.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 508.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1105 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1551.6665 | 196 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1880.2266 | 66.4 | 1 | 1 | 0250-Pulverizer feeders | SF-Startup Failure | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3581.6662 | 700 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.8833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6833 | 58.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.0333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.4667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.9498 | 351 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.5333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.2333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.1999 | 201 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.2 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162.3999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 273.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 294.9999 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 314.1333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 341 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360.25 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 362.4333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 495 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 501.165 | 111.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 523.3333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 557.9166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 751.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 796.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1278.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1302 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1307.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1326.5166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1555.1664 | 430 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1620 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1990.01 | 137.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2439.45 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2510 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.5833 | 95 | 1 | 4 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.8333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.5 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 23.6385 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 31.9815 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.8666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.8333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.5833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.9166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.6667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 95 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.2 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.998 | 124.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.1833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 143.1833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.3333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.8 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.6666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.4 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.9165 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 267.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 275.48 | 38.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 278.0833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288.2665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 332.7333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 429 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 470.8333 | 226 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 503.5 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.1665 | 247 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 539.4 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 553.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 606.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 647.8666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.75 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 769.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 793.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 798.25 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 949.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1033.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1094.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1469.1832 | 343 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1496.4 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1635.3999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4452.12 | 178.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.5333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.2 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.8 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.8 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.4667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.6665 | 232 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.6666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.4166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 48.7333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.5666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.8 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.0833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 72.904 | 56.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94.6831 | 299 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 96 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.6665 | 232 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 97.1832 | 343 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.5999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 118.4166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.1 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.2 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 143.0666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.9999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 163.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.0833 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 206.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 211.9331 | 374 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227 | 227 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 444 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.9942 | 211.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 542.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 553.978 | 120.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 605 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1270.7999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1288 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1375 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1413.4999 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1454.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1772.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2453.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2635 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3003.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.3999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.75 | 44.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.699 | 94.42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.0666 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.9 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 186.888 | 77.87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 227.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.7933 | 122.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 145.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 160.5833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.6333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 199.8333 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1924 | 240.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.4 | 31.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.7666 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1525.5 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.0667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.6 | 20.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 206.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 289 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 345.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1210 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.0333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 260 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 470 | 235 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2742.3333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 161 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 203.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 274.5 | 73.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 712 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4807.05 | 439 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4923.3331 | 700 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 679.233 | 497 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1428 | 255 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3079.9999 | 420 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4333 | 86 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.9 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.3833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3478 | 54.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.8 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.7333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.2333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.9 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.7833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.2499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.8 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.2 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126.75 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.3 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.5 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.9333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 277.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 375.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 388.8 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 415.1666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.65 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487.5 | 390 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 549.3833 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 601.0666 | 161 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 607.8666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 690.8666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 725 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 853.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 928.2 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3552.0831 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5652.5 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.1666 | 95 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6666 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.2833 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.9999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.5 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.1167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.15 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.65 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.4 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.1795 | 88.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 116.8 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118.56 | 98.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.65 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.5 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.6 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 269 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 333.0213 | 113.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 374.0445 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 408 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 425 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 447.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 464.8166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.8 | 282 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 540 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 569.5 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 609.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 704.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 708 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 818.605 | 30.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1143.6499 | 267 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1433.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1737.5166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2387 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2666.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2878.2 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3809 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6189.82 | 98.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9958.25 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.9332 | 176 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.55 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 45 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63.735 | 84.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.8332 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 84.3333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.8 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.7666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 104.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.0166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.5333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 189.55 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 325.6 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 333.45 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 353.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 435.9059 | 107.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 473.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 475 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 481.0832 | 251 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 568.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1064 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1544.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.8 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90.4666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 168.4625 | 134.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 176 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 366.6333 | 129.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 374.1 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 664.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 746.6666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.6166 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.0666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.74 | 58.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 159.081 | 122.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 188.15 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 389 | 97.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1539.2333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.25 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.6 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.0833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.95 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 218.7 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31 | 15.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 237.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 695 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 773.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.1 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.4166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 218.4 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.5832 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 280.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 316.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 328.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 313.7333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2073.5 | 638 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.21 | 32.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.4 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.7 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.4 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.13 | 50.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.25 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.25 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.55 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.1999 | 118.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.5666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.3 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.3 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.6 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.0936 | 56.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 97.6283 | 61.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.3167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 134.64 | 26.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.75 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141.1666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 185 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.6666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.3333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 209.0833 | 193 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 213.8999 | 207 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.3878 | 98.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.9918 | 68.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.1125 | 84.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258.5 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 283.9999 | 213 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 313.5 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.7666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.8499 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 349.0666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 357.5333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 394.8 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 395.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 429.3332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444.6 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 574.75 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 788.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 836.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 842.0832 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 937.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1069.95 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1220 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1256.58 | 140.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1504.7261 | 117.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1849.65 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2902.4 | 90.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3233.3333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3768.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5102.1666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10865.4164 | 445 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12738 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.6 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 13.1666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.1166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.8333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.4 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.6 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.9333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.5 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.9333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.03 | 71.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.8666 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.5833 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74.2333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.5 | 45.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.4999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124.15 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.6666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.5666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 174.1666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.8333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.2 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 234.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 236.7333 | 33.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.9999 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 322 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 387.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 449.6333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 537.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 551.8 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 610.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 646 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 688.55 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 835.6904 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 855 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 930 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 957.9 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 972 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1084.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1288 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1504.9999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2362 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.8 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.025 | 72.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.2166 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.9333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.95 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.2 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.6833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.75 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.4 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136.4999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140.5333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 151.4167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.9333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.3332 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 172.6667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 198.2866 | 84.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.5 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 254.8 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 287.4666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 335 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 403.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 467.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 472.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 489.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 587.4 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 589.6 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 637.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 651 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 767.9166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1317.3333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1983.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2378 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3702.8666 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 100.75 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 112.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1722.5 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2668 | 266.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.8833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.9 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.5333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 527.2667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 577.2 | 96.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.4 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.9 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 62.35 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.5333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.8 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 114.4 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1291.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1795.7333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.45 | 7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.1333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.2166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1702 | 74 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 264 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 266.5667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 584.9333 | 20.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 117.1664 | 370 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 267.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 368.4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 638.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 115 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 177.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 502.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 602.7 | 63 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1143.9973 | 81.52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.3666 | 251 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 186.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 206.25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 858.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7758.3332 | 490 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 143.3233 | 22.63 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 818.0998 | 486 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 295 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 88.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 61.1 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 175.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 427 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 501.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1361.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1188.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 156 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 617 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 155.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1211.8333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 82.3333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 22.75 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 537.5333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 291.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 23.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 50.1333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 312 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 522 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 251.3333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 60 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 548 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1043.3333 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.5 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.1 | 41 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 169 | 52 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.9 | 43 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 77 | 44 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 2 | 2 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.55 | 131 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 220.5166 | 131 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.3333 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 900 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 939.6 | 116 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2734.8 | 53 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65598 | 104 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 279 | 54 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 930 | 186 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.3333 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.0833 | 43 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 765.4 | 43 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.1 | 51 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 288.75 | 55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1095 | 150 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1557.4999 | 150 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.1667 | 17 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.1167 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.8333 | 95 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 599.5333 | 92 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 802.3166 | 161 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 294.6666 | 130 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 885.9583 | 96.65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 0.66667 | 1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.7 | 31 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198 | 27 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 609.5332 | 164 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2.8333 | 85 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.9 | 138 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.2 | 66 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6 | 42 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.5 | 26 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 75 | 125 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 943.2 | 108 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 579 | 96.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.45 | 17 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 184.807 | 108.71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.2333 | 98 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 236.375 | 30.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 267.5833 | 65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1018.9666 | 77 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1170 | 130 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1202.9833 | 89 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.0666 | 62 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.4167 | 17 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 168.5533 | 52.4 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 823.0831 | 595 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.9167 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 750.75 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1024 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183.3743 | 100.94 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.5333 | 14 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139.7332 | 131 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.8331 | 290 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287.4999 | 150 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1950 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.2 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 356.5 | 23 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 945.75 | 97 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.7666 | 173 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1635 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 404.5332 | 164 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 504 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.5 | 37 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1989.25 | 365 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.2667 | 2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 396.75 | 23 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 836.7331 | 308 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.3333 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90.6666 | 34 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 349.9999 | 120 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 18 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1556.3332 | 140 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 298 | 37.25 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 961.25 | 192.25 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.1785 | 39.03 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 10 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 158.01 | 52.67 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.9999 | 135 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416.6667 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 627.688 | 101.24 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1509.6667 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 475 | 95 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1043.84 | 130.48 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.4 | 6 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.25 | 25 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 243.295 | 24.7 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.35 | 127 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 296.8 | 212 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1356.6666 | 55 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2053.3333 | 55 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 938.075 | 71.7 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.9999 | 120 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.1666 | 37 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 909.9999 | 390 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 547.1333 | 116 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 683.4166 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 438.6666 | 80 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 490.4866 | 124.7 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.4999 | 90 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 419.4 | 108 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 90 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.3666 | 77 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.5832 | 227 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1140 | 120 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.3333 | 100 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 751.4866 | 66.7 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.8499 | 141 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.3333 | 20 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 593.75 | 62.5 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 50 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.66664 | 40 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17397.2 | 713 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7613.4165 | 515 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 770 | 140 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126.5832 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2568.9166 | 145 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.5833 | 175 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 40 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D3-Forced - Postponed | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 412.5 | 50 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 37.245 | 57.3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 536.4333 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1225.5333 | 62 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1473.9999 | 201 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9630 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 585 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4483.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 6 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.4 | 63 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 349.3499 | 153 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25041.94 | 70.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 902.5 | 57 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2525.8 | 34.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.4 | 31.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1187.9999 | 405 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8157.3329 | 1330 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112141.3996 | 588 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 131.8333 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4608.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4746.6664 | 400 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 2 | 5 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.5 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 426.4166 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 990 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 513.5999 | 288 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1315 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.4166 | 125 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7624.9995 | 750 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 24.36 | 25.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.25 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470.25 | 57 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 616 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1228.15 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2053.3331 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 8690.9163 | 499 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.75 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 250 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 436 | 545 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2712.15 | 63 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7648.3333 | 130 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9476.25 | 175 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.75 | 117 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 361.5999 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1780 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4178.3332 | 460 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 78.65 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1593.6 | 33.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13690.45 | 57 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.2 | 19.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414.7 | 31.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 165.75 | 85 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 2 | 4 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10680 | 30 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1938 | 570 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 465.4999 | 147 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1320 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1480.9333 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1722.2 | 316 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6303.75 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172.2667 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1303.0267 | 24.28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4837.2499 | 165 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1758.3332 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43158.5 | 418 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 2 | 5 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.18 | 25.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 454.1332 | 131 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.6667 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1 | 2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 538.4164 | 355 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 889.7 | 123 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1886.5 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2976 | 93 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.65 | 93 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.8 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1467.9332 | 388 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1973.3333 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2047.5 | 630 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11593.3332 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.2667 | 29 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.25 | 157 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 370.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3941.525 | 70.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.1666 | 170 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2580.8332 | 475 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 252 | 210 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 263.25 | 117 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 847 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1131.5 | 310 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6259 | 220 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14524.9998 | 300 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23767.6665 | 452 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.3666 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 571.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.3333 | 130 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 838.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1261 | 97 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1356.6665 | 440 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4230.4166 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 835 | 16.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 846 | 6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1170.8332 | 250 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 800 | 25 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 3 | 7 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 944.0333 | 127 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1062.7833 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3883 | 220 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.6666 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 236.6667 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1651.65 | 63 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 363.75 | 97 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2455 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3369.7997 | 498 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259.2 | 32.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 421.95 | 9.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6462.5 | 110 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99 | 22 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1627.965 | 116.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81.25 | 75 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1664.1499 | 249 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4656.6665 | 440 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 410.7499 | 159 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3038.4662 | 766 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238.5 | 265 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362 | 362 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 520 | 104 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1432 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.3666 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 305.2667 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1260.9999 | 156 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3367 | 130 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5315.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 13.0333 | 34 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 691.5333 | 44 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2652.75 | 131 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5804.47 | 70.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9947.49 | 70.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1010.6 | 32.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360 | 60 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.4999 | 75 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7586.2499 | 225 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.2333 | 17 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5427.99 | 603.11 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6688.4999 | 117 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4449.1831 | 383 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30637.4997 | 387 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65 | 260 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2724.5333 | 68 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6350.2664 | 388 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.8 | 10.6 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3753.75 | 165 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43964.25 | 219 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2520 | 120 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 876 | 438 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.3498 | 237 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.2 | 52 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 255 | 510 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5550 | 500 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2656 | 415 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3133.3532 | 220.4 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6162.1465 | 288.4 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5696.6833 | 139 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 111 | 18 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 164.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1047 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1574.5 | 470 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.5 | 85 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10531.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1560 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1964.7497 | 435 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 201.01 | 201.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1116.06 | 186.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1221 | 407 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1212.75 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13960.8333 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2946.383 | 65.33 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1806.21 | 86.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 572 | 286 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 146 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1796.6666 | 245 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1196 | 260 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 212.5 | 102 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 106085.9999 | 360 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2522.9635 | 316.69 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16388.5331 | 407 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 81 | 18 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.9333 | 88 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 238.3332 | 325 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1354.9164 | 355 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8.083 | 485 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.6 | 121 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.5833 | 77 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1229.15 | 403 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1456 | 280 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2150 | 40 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96 | 240 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 206.6132 | 238.4 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 282.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 302.1332 | 412 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 673.6665 | 470 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1650.2498 | 615 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2565 | 900 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50398.3333 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 352 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61241.5 | 530 | 1 | 1 | 0263-Primary air fan drives | U2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5400 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3173.3332 | 140 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216.6667 | 50 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 302.02 | 151.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 307.5125 | 246.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 678.03 | 226.01 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2643.2332 | 358 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31560.9664 | 842 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7450.133 | 458 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 658.6666 | 260 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501.4999 | 102 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1830.5833 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6271.9996 | 588 | 1 | 1 | 0264-Other primary air fan problems | SF-Startup Failure | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.9509 | 217.14 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.86 | 17.4 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 707.75 | 57 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1120 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 625.5999 | 408 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 814.9332 | 128 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1209.8333 | 238 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1186.6377 | 497.89 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4274.9333 | 184 | 1 | 1 | 0264-Other primary air fan problems | U3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.8333 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.2499 | 405 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3740.6331 | 383 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 181.8666 | 248 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.7833 | 187 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 383.9999 | 288 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10754.0664 | 388 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 25818.8997 | 801 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50537 | 388 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.75 | 57 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 48.75 | 25 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46 | 23 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2774.4 | 408 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6402 | 388 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24153 | 388 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.3333 | 17 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.4999 | 165 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.15 | 21 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.2666 | 86 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2006.6 | 508 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.3333 | 52 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.3333 | 110 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1040.3666 | 118 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 978.1332 | 262 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2442.0933 | 38.6 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 775.5 | 470 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.8 | 108 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.8499 | 177 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.45 | 67 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1195.8333 | 205 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.6 | 69 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.6 | 327 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 682 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 984.6665 | 211 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11865.9999 | 408 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.6 | 35.3 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 32.7167 | 30.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.9 | 21 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 472.9999 | 258 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 497.25 | 117 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 707.75 | 57 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 862.0583 | 35.5 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1495.9997 | 408 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.85 | 27 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.5 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 475.3332 | 155 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3154.6666 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1654.6665 | 365 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32171.6664 | 388 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.8 | 57 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 801.5666 | 34.6 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24443.5 | 589 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3018.3998 | 588 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2678.6661 | 820 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 9362.1332 | 268 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 650-Fluidized Bed
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 605.9333 | 122 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36340.9066 | 92.08 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15092.9331 | 721 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2226.5 | 73 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18092.5332 | 307 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.5 | 127 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.8 | 97 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21829.1333 | 187 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.3 | 82 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3077.8333 | 59 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | WECC | Winter | 110 | 12 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 800-Miscellaneous
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 402.25 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.1667 | 10 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1827.3333 | 10 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 526.2833 | 13 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6312.3333 | 10 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 671.1333 | 4 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288 | 6 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 371.6667 | 20 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480.4167 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.2 | 13 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.4 | 2.4 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 12.95 | 2.59 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.38 | 2.38 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 167.2 | 3.04 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 5.98 | 2.99 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 40.46 | 2.38 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 30.6332 | 3.41 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 87.12 | 3.63 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 2.44 | 2.44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 23.15 | 4.63 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 74.29 | 3.91 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.8333 | 65 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.75 | 131 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.8333 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.6 | 134 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.3 | 303 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 293 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 69.8363 | 39.53 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5625 | 41.25 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.05 | 99 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 422.7333 | 34 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 780 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1720.5 | 74 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.25 | 175 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51.7166 | 107 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.8332 | 125 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2640.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 530.0999 | 205.2 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2550 | 170 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5936.0265 | 746.67 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2288.4995 | 690 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.9999 | 210 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.8664 | 352 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1185 | 237 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5517.9999 | 186 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.9 | 139 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.3333 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65.8 | 329 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 308.9166 | 55 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168.75 | 125 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 473.0333 | 23 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 961.2 | 108 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 641.6666 | 154 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 276 | 138 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124 | 120 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 620.6667 | 35 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.1 | 102 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.3 | 94 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1583.9999 | 108 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1417.9164 | 415 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.2499 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 96 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 960 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.5 | 90 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 766.9666 | 173 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1359 | 108 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 145 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 27 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.8 | 76 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.5 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 567.6666 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1148.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.1667 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.5 | 79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1639 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 154.1 | 69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 666.6666 | 200 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1123.75 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1848 | 96 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 512 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1054 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0.46665 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115.2667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.8666 | 94 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 589.9622 | 165.41 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14289.8 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.2 | 21.6 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.8333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8719.9999 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 532.8333 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8488.3332 | 550 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14271.3997 | 858 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.8166 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.095 | 114.9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.75 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 973.3333 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1350.1833 | 71 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3570.6665 | 416 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 557.75 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 733.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 874.5833 | 5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86.9166 | 149 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 637.8332 | 215 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9319.9167 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17101.4666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.2 | 16 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 140 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7827.8166 | 191 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.6 | 57 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14007 | 609 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40594.6665 | 416 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.8 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 872.2 | 89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.1333 | 76 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124.5 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 623 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 636 | 53 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 695.5666 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 777.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3951.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 261 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 598.5 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62.4 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 722 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 205.8 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96982.5 | 670 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18575.6663 | 532 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66 | 88 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.2016 | 66.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147.3333 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.2499 | 165 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 200.6666 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 835.9998 | 228 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 148.8333 | 94 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1045.8 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 445 | 89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.64 | 40.41 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 216.75 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.25 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 580 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5761.2499 | 165 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.25 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.7816 | 109.9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12994.9999 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.4 | 33 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 296.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 679 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 685.1333 | 172 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 826 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1690.5 | 138 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 936 | 156 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 844.2 | 13.4 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 846.4 | 36.8 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14436.6663 | 610 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36671.25 | 825 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.6667 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 960.6666 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2445.7499 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2601.9 | 177 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.875 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.6331 | 278 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 180 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1300 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2619.867 | 117.22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5260.2666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3000 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 871.8733 | 109.9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 160.4166 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1213.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1473.3333 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1639.1667 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7066.4 | 292 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 680 | 170 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.5333 | 109.9 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2753.6666 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 267.5 | 75 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 851-CC GT units
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98 | 98 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106 | 106 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121 | 121 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176 | 176 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181 | 181 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184 | 184 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.5666 | 131 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 705 | 235 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 926 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2409.1666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2469.93 | 14.79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1106.5299 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3000 | 125 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20.4795 | 29.97 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99 | 132 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.24 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.9 | 39 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8023.4 | 77 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.0899 | 83.1 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123761.9329 | 614 | 1 | 1 | 0280-Pulverizer fires | U2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.3 | 23 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.5 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.8355 | 136.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133 | 133 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160 | 160 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187 | 187 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 188 | 188 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 215.8332 | 185 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3931.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.7869 | 144.33 | 1 | 2 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.9999 | 102 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2104.5 | 45 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.7499 | 135 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 234.4215 | 161.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13078 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.6666 | 95 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.8789 | 149.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.5576 | 136.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268 | 268 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1264.39 | 136.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5380 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.7333 | 44 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 219 | 45 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 309.3333 | 58 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 363.9999 | 156 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 445.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.3815 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.9833 | 101 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.6666 | 52 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.8333 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134 | 134 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148 | 148 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 345 | 115 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472 | 118 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 492 | 123 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 681.9999 | 186 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4465.5 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.9166 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1112.4 | 103 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2419.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6457.3333 | 145 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.072 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.8345 | 136.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.4913 | 90.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.5 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 305.9999 | 135 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 902.8616 | 133.1 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.345 | 68.1 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.4 | 32 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 222 | 222 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 246 | 246 | 1 | 2 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252 | 252 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 404 | 202 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 924 | 231 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.6213 | 107.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 917.5833 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32940 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.3539 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.1304 | 155.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1269 | 141 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.67 | 89.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.5 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205 | 205 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 261.34 | 130.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 402 | 134 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2164.1666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2292.5 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.677 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.85 | 39 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15890.9999 | 180 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43035 | 151 | 1 | 1 | 0280-Pulverizer fires | U2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138 | 138 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143 | 143 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145 | 145 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153 | 153 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182 | 182 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 195 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211 | 211 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 263 | 263 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 282 | 282 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 895.3333 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2394 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 36.12 | 25.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7595 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18655.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.9792 | 160.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2023.84 | 29.12 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8285.8331 | 305 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33879.5332 | 532 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 105 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109 | 109 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189 | 189 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196 | 196 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.6666 | 200 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.6529 | 144.33 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17295.3333 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 316.1667 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368 | 32 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 670.7415 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 831.25 | 133 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2880 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3850 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.5833 | 95 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 4 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 215 | 60 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 60 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1406.8666 | 94 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 18 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.3333 | 104 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.6666 | 40 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 530 | 60 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 512.5 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 33 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 202.523 | 130.66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 911.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1200 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7820 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.3333 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.6 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3572 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15428.2333 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.4666 | 88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.9167 | 23 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 415.9999 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 826.672 | 58.08 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 384.4896 | 69.07 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.75 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1125.4209 | 86.46 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.1 | 27 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.4165 | 295 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 299.25 | 315 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1440.96 | 75.84 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3160 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.6333 | 58 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 218.31 | 114.9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3472 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4414.6666 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 306.9516 | 141.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 672 | 224 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4992.1625 | 100.75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 965.669 | 129.62 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.1 | 46.1 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2340 | 180 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 298.6666 | 140 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1794 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.0833 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2496.9164 | 415 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7727 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7789.45 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.6667 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 245.735 | 123.9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 317.75 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 447.3333 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2400.9 | 151 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.9999 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.1166 | 67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 2 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 340 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6262.5 | 167 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 243.75 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.55 | 291 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1939.5999 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.6 | 4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 870 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 684.5832 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2428.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2441.1333 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7597 | 214 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2526.7 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.4 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 239.75 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.0833 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34 | 17 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 148.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 795.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 936.8333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.2167 | 29 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 660 | 240 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1235.6666 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1633.5 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 320.215 | 78.42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.5333 | 71.44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.6666 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 211.0266 | 74.48 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.75 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.3333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.25 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4929 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 583 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 890.6666 | 64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1239 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4699.3333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8569.4166 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3 | 22.66 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 287.56 | 71.89 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.2058 | 31.91 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2851.6663 | 580 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 3 | 6 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.3 | 63 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 431.2 | 308 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 850.6166 | 161 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6157 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.1 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 664.4166 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7062 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94 | 47 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2108 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.75 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.0833 | 13 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257.5 | 206 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2415 | 140 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2777.25 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5219.4666 | 296 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9628.6665 | 286 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.4667 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1002.8 | 6 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 607.1016 | 64.7 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7812.9999 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.3333 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 117 | 52 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1302.2 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 237 | 79 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1152 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 298.3333 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.3666 | 52.6 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116.413 | 61.27 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 902.4998 | 570 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1645.65 | 477 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.85 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.3166 | 68.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.9332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 144.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.8333 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.2833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.6 | 197 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.7166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210.7333 | 116 | 1 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.8665 | 208 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 280.6 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 377.34 | 132.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390.5333 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 417.5643 | 72.41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 520 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 575.1667 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 662.3166 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665.4665 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 694.75 | 397 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 747.9999 | 408 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 863.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 864.1867 | 36.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1005.6266 | 175.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1126.4333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1135.7499 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1354.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1355.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1475 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1519.5333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2316.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2884.1165 | 413 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3048 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4904.1666 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28431.0833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.6167 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43 | 215 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6667 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.9166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.1167 | 21.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.6666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325.8366 | 81.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.6666 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 375.4166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 465.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 472.0333 | 238 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 616.9167 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 766.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 806.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 919.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1187.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1268.615 | 34.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2860 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3228.75 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20214.3333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21581.9999 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.5333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 111.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 173.9 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 254.3332 | 218 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 320 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 335.3533 | 37.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 339.9999 | 204 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 347.7333 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 563.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 596.9166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 714.9333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1127 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1171.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1232.6664 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2715.7499 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4407.5 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4695 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.0667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.9667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.3 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 532.9499 | 153 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 832.9999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 220.05 | 163 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 411.23 | 35.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1712.3133 | 49.04 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 567.474 | 32.52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 960 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2402.4457 | 134.09 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.1 | 137 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.4217 | 24.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.8666 | 224 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 348 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 690 | 230 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 888.8 | 66 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 958 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.7333 | 59 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.4 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 266.9 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3798 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.7333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20.7667 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20406 | 57 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 100 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 933.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5073 | 57 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 453.629 | 264.25 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.55 | 171 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.52 | 20.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.2675 | 93.69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.4333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.3333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.55 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.9998 | 288 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.3332 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 417.5 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 476.82 | 32.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 485.3333 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 535.1665 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 561 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.7499 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 636.5666 | 338 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 747.5 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 851.4931 | 690.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1072.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1149.5 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1249.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1569 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2047.3333 | 166 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2699 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3034.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6787.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10115 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22499.1666 | 350 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.8332 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.1333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.7333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.1499 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.75 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.7499 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 192.1333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 231.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 244.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 249.75 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 284.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 304 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 344.7 | 114.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 412 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 454.675 | 139.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 479.9998 | 288 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 693.8332 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 792.6665 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 871.45 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 895.3333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1647.1 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1689.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1840.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2053.0066 | 51.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2072 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2922.4 | 281 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8281.2 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.6666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.6666 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.6167 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184 | 184 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 211.75 | 121 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 292.6 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 373.7867 | 17.12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 530.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 741 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 776.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 836 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 871.0999 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1092.0466 | 66.86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1219 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1244.4 | 408 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1848 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5913.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28093.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.8667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.4 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 243.1975 | 74.83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 555.5083 | 95.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 2 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.9 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.9666 | 154 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2899.65 | 117 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4646.01 | 37.02 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 891 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.8667 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 203.4666 | 109 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2934.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5106 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2758.35 | 497 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1813 | 740 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.7333 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.1533 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.5833 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.4136 | 99.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.2499 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.5 | 223 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.35 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134.16 | 46.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.9733 | 30.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 202.3999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.6 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 403.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 405.081 | 33.34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 504.47 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 526.6999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 557.75 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1290.1166 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1488.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4658.2666 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29570.3332 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.3333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.9 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.2499 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 128.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.5166 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170.4 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 227.3333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 322.1333 | 151 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 341 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.0833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 461.45 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 486.55 | 263 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 491.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 711 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 748 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 937.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 938.5108 | 23.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1058 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1122 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1125.8333 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1231.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1300 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1308.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2146 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2254 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2665 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2725.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3362.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5886.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6950.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12981.7599 | 138.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26.9167 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.5 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.6 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160.8608 | 70.45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 176.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 179.854 | 47.33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 265.5 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.9666 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 480.1666 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 547.6666 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 606 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 746.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 776.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 833 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 917.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1099.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1197 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1363.2319 | 176.28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1879.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2171 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4576 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22195.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31855 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 103.8667 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 112.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.35 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 116.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.566 | 80.76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1980 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7055 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1366.55 | 30.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1648.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 322.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 387.4833 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.4667 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.2 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.9 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 335 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.6926 | 58.94 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8268.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3624.9997 | 750 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7946.1663 | 490 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12166.5995 | 762 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.1167 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.0833 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.6999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.4909 | 188.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.3333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.9999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 239.7966 | 60.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.0833 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 368.5733 | 50.26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 418 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 460.62 | 32.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 487.9 | 238 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 546 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 583.1 | 238 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 630 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 662.0833 | 45.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 780 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 812.04 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 850.7 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1155 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1364 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1907.1 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2001.9999 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2263.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3045 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6768 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.4133 | 42.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.5 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.5 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.5 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 184.7533 | 51.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289.0666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 337.75 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 388 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 400 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 470.71 | 61.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 500 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 743.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 913.045 | 39.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1001 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1320 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1485.61 | 39.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2340.8666 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3163.1 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4493.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15004.6166 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43495.4666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 2 | 6 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.05 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.0833 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 173.3333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 241.5 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.6666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 400 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 523.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 552.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 555 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 799.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1069.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1181.7 | 234 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1370.8332 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2323.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3986.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10668.1333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.75 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.2 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 383.7667 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 995.9 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 69.5166 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.8666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3780 | 189 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.3333 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.2 | 54 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 234.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3518.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 101.5 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1239.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.7333 | 133 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2829.4 | 84 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1830.6308 | 262.77 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2650.5 | 90 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14823.75 | 335 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.25 | 17.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.64 | 71.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.1499 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.1666 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.6833 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.6433 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204.05 | 31.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 228.2666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248.6 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270.1 | 111 | 1 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290.4 | 121 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 308.3333 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.3333 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 455.1 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 572 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.75 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 613.9467 | 36.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678.9333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 683.65 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 708.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 850 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 933.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 940.0666 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1033.75 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1937.1999 | 200.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2204 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2205 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2388.75 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2440.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3425 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4932.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5479.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6561.3331 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7445.75 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8710 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18474.7 | 71.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24862.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.0666 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.0466 | 75.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 74.6666 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.8 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.9333 | 229 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 193.3333 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.9 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.57 | 31.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.4899 | 181.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 270.4151 | 118.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 284.8066 | 71.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.8 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 363 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 364 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 393.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 401.8666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 425.25 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 435 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 465 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 525 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 607.6833 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1111.2499 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1248.38 | 51.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1443 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1912.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2433.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6902 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16812.05 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42428.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20.57 | 205.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.3 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 134.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 159.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 161.2 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 178.5 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 219 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 252.8166 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 386.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 412.7999 | 288 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 566 | 283 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 605.1999 | 408 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 682.0733 | 52.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1226.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1455.6 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1698.7666 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2711.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2893 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4181.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5250.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 8583.5166 | 203 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1174.8 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 62.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 247.0666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3392.0332 | 319 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 255.75 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1815 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8476.9576 | 131.29 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 376.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.7667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.5333 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 244.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.3666 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 323.9166 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 403 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 618.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2675 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3989.4499 | 219 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 212.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.3 | 762 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 6 | 16 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.5833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.1 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.9166 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.3333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.4 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.5 | 197 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.75 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.48 | 125.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.3633 | 37.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 219.9225 | 125.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 230.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297.5 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 456 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475.9999 | 357 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 477 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 536.5599 | 211.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 554.1825 | 116.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 584.64 | 162.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 697.2833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1365 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1426 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2321 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2872.0666 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3701.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4051.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9794.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31245.5 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.01 | 10.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.4333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.8333 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.15 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.5 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.2545 | 50.61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.5 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.7 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.2166 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.4 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 236.5 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 258 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 479.4 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.9333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 645 | 215 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 708.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 902 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1002.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1217 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1496.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1639.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1652.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2375.95 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2650 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3022.9166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3989.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6524 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13687.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 15.75 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.45 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.5 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.0166 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 192 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 243 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248.7333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 325.8332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 338.25 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 368 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 436.5 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 468.6 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 510 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 534.0833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 695.8333 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 868.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 954 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 984.7 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1190.6665 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1404 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1932.3332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2365.2 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2385 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2494.2666 | 104 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6820 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12217.4997 | 405 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.6 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2349.3 | 382 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5542.4999 | 225 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.7 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.45 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 811.5166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.5285 | 59.31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1115.625 | 212.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1978.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.95 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5756.8 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.5 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.8666 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 148.5166 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 243.7666 | 71 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1293.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3011.1666 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3059.5833 | 175 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.3193 | 81.02 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 306.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1049.6666 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1872 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2240.1126 | 70.04 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1573.833 | 497 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8963.9 | 814.9 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6666 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.8667 | 10.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.5 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.8667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.7 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.6667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.1866 | 30.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 154 | 154 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.4472 | 196.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.6666 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 197 | 197 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.333 | 560 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 271.3332 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 282.73 | 115.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 313.3665 | 238 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 323.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 338 | 338 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 422.5 | 338 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 448.1767 | 37.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 461.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 534 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 548 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 682.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 758.8333 | 157 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 851.1533 | 85.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1101.6 | 408 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1108.33 | 161.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1385.75 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3444.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3480.6666 | 227 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3867.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.5 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.4166 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.6667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.75 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.9165 | 199 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.8916 | 82.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.25 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 249.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 273.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 302.9999 | 181.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 520.65 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 532.15 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 783 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 794.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 830.7 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 847.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 868.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1213.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1281.5 | 233 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1547.2165 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2127.5 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4367.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8925 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80114.9166 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.87 | 178.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108.5 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 117 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 168 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 219 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 352.8 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 392 | 224 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 477.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525.9666 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 562 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 756.4999 | 267 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 955.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1722.24 | 147.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1960 | 400 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2762 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3909.9333 | 223 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4259.4 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.6833 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 153 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 972.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1111.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.7833 | 151 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 72 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 653 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2047.3 | 118 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3060 | 180 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 756.0833 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1785 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.3333 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 325.0833 | 235 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 399.5 | 235 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2871.7666 | 101 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8548.3329 | 575 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.6 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.7 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.3333 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.0833 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.3332 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.0667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.75 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 113.0585 | 144.33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.1666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.0133 | 30.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 156 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.3333 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 208.3667 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 264 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 283.9366 | 165.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.8533 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 356.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 357 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.2333 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 559.6666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 589.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 632 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 659.45 | 121 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 779.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 800 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 881.2833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1108.38 | 46.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1213.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1752.6 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2231.8667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2522.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3321.35 | 183.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5006.5 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14902.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.85 | 211 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.5999 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.45 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.2167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.3916 | 125.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 337.1665 | 238 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 533.54 | 51.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 633.3333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 990.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1031.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1033.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1415.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1569.3999 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1755 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2090 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2295 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6915.3333 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7666.7499 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.9499 | 159 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.6666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.8867 | 19.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90.75 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 144.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161.85 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 171 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 255 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 258.5 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 418.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 713 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1291.9997 | 408 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1444.3999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2322 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3228.25 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.5333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.3666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.7 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.65 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.5066 | 66.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1971.45 | 337 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 427.7693 | 110.63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.2666 | 111.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 621 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 680 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 775 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2491.6666 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 98.8 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2368 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 532.2749 | 135.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 672 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2424 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.35 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.15 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.65 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2524 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.7833 | 89 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 338.3333 | 175 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 415.9166 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.4666 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 211.6 | 69 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 286.5333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48 | 15 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 20 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 552 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 1017.575 | 131.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3729.1664 | 358 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 514.6 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 267.4666 | 118 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 321.8666 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 319.8 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 934.8332 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 183.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1622.5 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265.5 | 118 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4340 | 140 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.5 | 10 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.5 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2600 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2763.1499 | 117 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305.0833 | 35 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 5 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3012.5 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4216.6666 | 40 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.3333 | 196 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 302.8333 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 627.8999 | 117 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 944.1666 | 110 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2672 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.1 | 46 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475 | 250 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 701.0666 | 176 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2980 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38200 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10 | 20 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 825 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1454.8332 | 301 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 10 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42 | 70 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.9166 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.6667 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.75 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 449.1666 | 110 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18620 | 490 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 354 | 118 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3793 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.4 | 114 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.6666 | 176 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308 | 112 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1391.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1086.9833 | 77 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1770 | 120 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138 | 46 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1378 | 106 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2946.5 | 415 | 1 | 1 | 0313-Pulverizer mill trunnion seals | U1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 468.75 | 125 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4083.125 | 130.66 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4464.2166 | 130.66 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1003.4 | 58 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4769.9166 | 65 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 345 | 46 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0314 | Pulverizer mill ball charger hopper (ball mills only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224 | 28 | 1 | 1 | 0314-Pulverizer mill ball charger hopper (ball mills only) | D2-Forced - Delayed | 100-Fossil-Steam
0314 | Pulverizer mill ball charger hopper (ball mills only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 384.1 | 46 | 1 | 1 | 0314-Pulverizer mill ball charger hopper (ball mills only) | D1-Forced - Immediate | 100-Fossil-Steam
0314 | Pulverizer mill ball charger hopper (ball mills only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 444.6666 | 46 | 1 | 1 | 0314-Pulverizer mill ball charger hopper (ball mills only) | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 551.4667 | 47 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3568.95 | 77 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 7 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 833.3333 | 125 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.3333 | 16 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.8 | 36 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 254.8 | 52 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3117.6 | 72 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.0666 | 64 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6219.1666 | 170 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 528.9 | 82 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.85 | 37 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 420 | 72 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 180 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.8666 | 62 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 166.25 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 844.7999 | 144 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 879.9999 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.9998 | 282 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.6 | 126 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 355 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 726 | 121 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 879.6666 | 91 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 807 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.45 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 274.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.4 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 214.1333 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2822.9166 | 125 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 261.4666 | 296 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 658 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2562 | 61 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.0667 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1500.3332 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1619.1 | 38.55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.8286 | 52.28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.7 | 237 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.65 | 81 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.3333 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 135 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1343.6666 | 145 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.5 | 24.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.65 | 47 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 123.3333 | 148 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 140.43 | 45.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 350.75 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1443.6833 | 97 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2437.5 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1151.865 | 209.43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.6498 | 237 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.6666 | 89 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.25 | 13 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.9999 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 401.9166 | 91 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1228.95 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 175.56 | 136.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 194.75 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 302 | 45.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 721.56 | 171.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3925.9999 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10857.1666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4212.9 | 67.95 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308.58 | 44.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 243.9 | 8.13 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441 | 210 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5397.5 | 75 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.8333 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.6333 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.7999 | 204 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.9332 | 436 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 368.4999 | 201 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 853.6666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79 | 15.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.8 | 16.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.5 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34 | 6.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.6666 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 908.6666 | 116 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.5833 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.8 | 81 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.25 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 426 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 524.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.3333 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 512.5 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 546 | 126 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 422.75 | 16.91 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.56 | 20.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 483.455 | 50.89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.55 | 127 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312.6333 | 166 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.1333 | 116 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.2 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.2666 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.6666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 173.25 | 33 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1249.5 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 418 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.6666 | 95 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.7 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.6 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.5 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 586.5 | 85 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 902.5 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.7667 | 22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108.3333 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 730.5833 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1200.8333 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.1716 | 34.3 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.9 | 129 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.8261 | 140.33 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.8999 | 129 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11145.2666 | 188 | 1 | 1 | 0325-Pulverizer skidding | U1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 489 | 20 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 900 | 120 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.06 | 36.12 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.2 | 129 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135.252 | 159.12 | 1 | 1 | 0325-Pulverizer skidding | U1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 600 | 16 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 336 | 42 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1421.35 | 131 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1560 | 78 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.7 | 51 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 260 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 363.05 | 137 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.8333 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 399 | 57 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 687 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 833.75 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3502.6664 | 370 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.8666 | 104 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 716.1333 | 82 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.5 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 275.9166 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 613.3333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6884 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.4 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 3 | 4 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46 | 23 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.6667 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1588.5333 | 112 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1575 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 117.0166 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 426 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 464.8 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.8 | 87 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 185.25 | 39 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.4999 | 111 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1038.5 | 62 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.5 | 79 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 224.7 | 126 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 292.2665 | 274 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 833.75 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.3333 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 2 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.3333 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 283.3333 | 250 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 605.6666 | 230 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1218 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1868.75 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.8167 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 519 | 173 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 753.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 494 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 455.3 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.0166 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 352.9166 | 275 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 483.9333 | 119 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 539.9166 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 390.4999 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6490.8999 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | U1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.5164 | 98.67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 392 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 870 | 87 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1834 | 280 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.05 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.25 | 21 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 492.3333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 943.029 | 59.31 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60938.5 | 230 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.88 | 28.47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.3333 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.9999 | 195 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.75 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.1333 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 142.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 227.8 | 67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 459.0168 | 135.67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1624.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 317.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1765 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4151.5833 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.75 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2040 | 170 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 281.2 | 74 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 435.7499 | 315 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.6666 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 160.8 | 67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 325.2666 | 119 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357.5 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 357.5 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 575 | 230 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.5 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 286.4167 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.4166 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1217.0833 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 208 | 26 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.9333 | 22 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.2 | 52 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.25 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 227.3333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 456.6665 | 274 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 68 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 96.3333 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.46666 | 7 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.6 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 168 | 63 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6785 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.3666 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.5 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 764.6666 | 124 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 856.2509 | 75.33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.7333 | 52 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 227.7333 | 61 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98 | 56 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 143 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 128.2833 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154 | 77 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.2 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4387.5 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1137.5 | 91 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3223.8333 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70255.9999 | 240 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.6666 | 140 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2440 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 144 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 269.7 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2474.6666 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.25 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56 | 112 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.8167 | 13 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1683 | 67.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.0666 | 128 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 399 | 38 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 440.1116 | 76.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 296.3333 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.7499 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 586 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5344 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.9166 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 208 | 208 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 334.46 | 47.78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 610.6666 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 941.3999 | 108 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.6 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.25 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.2 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.4 | 9.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 172.0665 | 178 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 175.75 | 111 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.5833 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 526.5 | 81 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 104.3 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.9166 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.5 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 895 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.75 | 69 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3166.6665 | 500 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.3333 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 697.3166 | 43 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.6667 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 415.2 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1388.3333 | 119 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1657.698 | 163.32 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.1759 | 109.92 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 134.75 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6199.9999 | 240 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | SF-Startup Failure | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.4 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 738.8333 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.9 | 86 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 512 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 870 | 300 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1221.3333 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 179.0666 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.1666 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 172.6666 | 140 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 851.6666 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.3666 | 61 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.9166 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.5 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.75 | 69 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.75 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.9999 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 129.15 | 63 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2156.5 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 506.6666 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.8666 | 29.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 396.75 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 440.1667 | 38 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 969 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6060.4 | 139 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2968 | 106 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 2 | 2 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 115.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.3666 | 46 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 37.5 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4.5333 | 68 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 294.4999 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1377 | 162 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7276.1 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.25 | 5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 216 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.7333 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 405.65 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.8667 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.5833 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 410.6666 | 224 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.2 | 34 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260.3 | 274 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 506.94 | 149.1 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.9 | 54 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 185.25 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 564 | 141 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 744.9 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1066 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 188.7833 | 47 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 207.4333 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 776 | 38.8 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 455.3 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.6666 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.5833 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 491.8666 | 124 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 541.7573 | 134.32 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.5333 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 68.4666 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 190.1 | 38.02 | 2 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 275.5 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 316.25 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 458.1865 | 227.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 134.3333 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.9167 | 5 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.0833 | 163 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 261 | 116 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 573.3333 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 30.8 | 56 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.6666 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 379.4166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 464.2166 | 173 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 683.7 | 106 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45.0666 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 533.75 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 321.3 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 411.3333 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.8333 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 267.15 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 663 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1496 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2295 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11814 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.9333 | 148 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.1 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.75 | 111 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 947.8333 | 121 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.9166 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 965.0666 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2725 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 205.6333 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 503.7621 | 156.61 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 547.2 | 30.4 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 231.1666 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.4333 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.8332 | 370 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192.4 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.0167 | 11 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 153 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.9666 | 182 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 381.3333 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 394.45 | 161 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 597.9165 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 617.3999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1189.9 | 163 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.3667 | 23 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.2332 | 158 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.75 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.8166 | 133 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 39.3466 | 59.02 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48.4499 | 171 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82.4999 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 374.2933 | 46.4 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1422.3333 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.1833 | 71 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.3 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.8332 | 143.75 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.2166 | 161 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.8333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 147.5166 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376.5667 | 22 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 230.3 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.45 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.9998 | 282 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 726 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.8 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289 | 102 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.25 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 456.3 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 78.04 | 58.53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.5333 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 383.3333 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 496.5999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2154 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 272 | 136 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 228.99 | 76.33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 156.3166 | 113 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 529.0666 | 124 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.5833 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.25 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 655.0333 | 86 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1979.9999 | 216 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390.588 | 88.77 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165.3166 | 91 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8.386 | 71.88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.8446 | 105.22 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 226.1666 | 118 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450.9999 | 246 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 779.1 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1026.9999 | 237 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1087.8333 | 214 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1460.25 | 177 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.2 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.8928 | 76.33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.0999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.2 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 353.5 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 728.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1047.2499 | 213 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1440 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 376.8333 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 118.25 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 422.9999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.6666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.5167 | 29 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.2666 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 948.5775 | 54.99 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8063.1 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1083.3333 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1899.9997 | 750 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 636.1666 | 110 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.0055 | 85.73 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 147.8516 | 66.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 207.5 | 41.5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 238.5 | 106 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.4975 | 79.33 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.75 | 87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.95 | 49 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 172.8 | 54 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 845 | 130 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.4999 | 150 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 395.8333 | 250 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 749.3333 | 160 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1586.2333 | 46 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5265 | 135 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.4 | 87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.3416 | 70.01 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105 | 70 | 2 | 2 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 236.0088 | 232.14 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.5833 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 78.75 | 135 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.6666 | 28 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1726.6666 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2490.375 | 8.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.6667 | 10 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.65 | 143 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.185 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1869.5999 | 171 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.75 | 87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24.5333 | 73.6 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30.4167 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.6 | 153 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.3333 | 130 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168.9999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.5 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.8633 | 66.74 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.9125 | 67.95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.5 | 125 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2919.7 | 86 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.25 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.5667 | 23 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168.495 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 253.34 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 440.955 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3827.585 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.5 | 10 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.9 | 106 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.7333 | 151 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.8385 | 57.13 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.9993 | 139.09 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 173.4993 | 176.44 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.725 | 55.15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.4999 | 150 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1998 | 1110 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.4166 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.6666 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 417.0658 | 18.55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 564 | 240 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1514.065 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 120.4466 | 81.2 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 367.7333 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1372.0832 | 185 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 352.9166 | 121 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.95 | 63.3 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2780.765 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5751.535 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.8 | 108 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.8999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135.035 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 224.55 | 499 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 728.7 | 18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1714.19 | 66.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2335.5 | 81 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.9024 | 78.99 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.8416 | 86.02 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.6666 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 485.25 | 64.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 686.0667 | 41 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 980 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1028.7 | 254 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2136.66 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 125.3 | 179 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 246.4 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 699.6 | 106 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 833 | 196 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1100 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1177 | 107 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7210.9333 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.9432 | 257.83 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.4975 | 57.27 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6208.455 | 216.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 194.1 | 64.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 286.8 | 71.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 393.3333 | 118 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2382.9167 | 19 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.15 | 57 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5478.3332 | 475 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.4 | 87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 74.2 | 63.6 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 323.5 | 64.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.5333 | 77 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 997.5 | 21 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 140 | 70 | 2 | 2 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22916 | 170 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.5999 | 216 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26531.6999 | 234 | 1 | 1 | 0339-Pulverizer System Puff | U3-Forced - Postponed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 250.85 | 87 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11979 | 132 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1150.785 | 71.7 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1974.9833 | 71 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 317.73 | 90.78 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 678 | 226 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 3 | 3 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.25 | 67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141.6666 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.2 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.375 | 120.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 228 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.25 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 486 | 324 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 846.8308 | 60.13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 912.0833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1333.8 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3462 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3910 | 230 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5885.5 | 74.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6095.1999 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16529.6 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.2166 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.3 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.1167 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.9167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.4833 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1050 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1161.2999 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2246.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2424.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3128.4167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3906.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13342.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.7 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.9999 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 258.6 | 86.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 349 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 519.5832 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1235 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1316 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1680 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1869.9998 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1916.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2230.3833 | 163 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4986.5833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20760 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 174.99 | 58.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 524.0499 | 141 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.3 | 40.1 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.85 | 17.7 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.65 | 17.7 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 845 | 50 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.9833 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.075 | 76.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.0025 | 90.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 486.9333 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 693.55 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 766.8333 | 107 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 844.75 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 962.8666 | 101 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1335.5999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3040 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3752 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8470 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61 | 1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 298.7 | 103 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 326.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480.9 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 491.5166 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 552 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 791.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 814.9167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1036.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1225 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1485 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1781.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4957.7332 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11776 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.835 | 43.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.7667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.2375 | 52.19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 234.9499 | 111 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 284.2 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 691.5833 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 736.9166 | 185 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 958.5333 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1060 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2400 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1842.95 | 29 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.445 | 14.1 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4883.2 | 44.8 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 873.2833 | 34.7 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 801.3866 | 109.28 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.0333 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.8 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.9833 | 229 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.8333 | 67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.9166 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.7998 | 288 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259.25 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 589.9831 | 389 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 704.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1250.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1252 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4255.2666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7919.1666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.8333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.67 | 18.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.6666 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227.8 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 348 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 638 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 735 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 899.9666 | 203 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 904 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 918.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1150 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2266.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2517.9 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4650 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5035 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9038.4 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.96 | 25.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.4 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 117.1666 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.8 | 17.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146.2333 | 107 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.8 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1402 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.1 | 37.55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 326.4 | 81.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 504.6 | 168.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1073.05 | 97.55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 282 | 18.8 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.6033 | 24.2 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.1667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.0533 | 34.4 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.74 | 25.2 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.9333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.9333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.8 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.25 | 157 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 238.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255.6666 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 268.2 | 298 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.5 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.4999 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 418 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 584.9999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 734.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 891.9166 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13633.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.8 | 111 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.5 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.3666 | 167 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.7166 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191 | 95.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.1666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 471.25 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 657 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679.3665 | 178 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1683 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1756.2499 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3765.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10176 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.5833 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.936 | 43.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.3 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.9999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.8 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 487.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 913.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1050 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1214 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3103.5333 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4310.8 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.5 | 79.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231 | 3.5 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459.9 | 18.9 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 498.8 | 116 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2235.9 | 87 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.8 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.505 | 43.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 252.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 297.7333 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.9167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 435.0833 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 821.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 826 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 920 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1938 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2028.2499 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2597 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30310 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35427.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.1333 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.65 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.8333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.4999 | 183 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.5 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 317 | 79.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 568.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 715.0666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1100 | 176 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1474.6 | 292 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2632.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2717 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15705 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.75 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.7167 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.1149 | 80.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 212.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 370.3333 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 430.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 487.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 611.2666 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 633.5 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 896.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1038.5 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1400 | 350 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1796 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9300 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.48 | 57.48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.01 | 113.01 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 268.8475 | 104.07 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 135 | 67.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.18 | 3.8 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.9 | 6.1 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 293.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3262.2333 | 77 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.25 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.3332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.7999 | 408 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.28 | 109.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.25 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 333 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 381.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.8333 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1044.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1592.325 | 141.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1855 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3728.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4560.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12336.2832 | 307 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.9166 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.2666 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.8 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.5166 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.0831 | 395 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.9166 | 151 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.8 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 164.6666 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 193.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342.8999 | 162 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360.9833 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 387.5666 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 506 | 132 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1833.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.12 | 25.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.5 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.7 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195.4999 | 138 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.8 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 252.7 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.3333 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 545.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 993.6 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1647.9166 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3022.9333 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7146.1666 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.74 | 48.37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.84 | 25.2 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.0665 | 184 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.1666 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.4666 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5833 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.4999 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.7999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.7166 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.5 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 123.625 | 64.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.1116 | 101.59 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 472.0333 | 238 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 555.3333 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 588.3 | 196.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1051.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1398.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1425 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2300 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2333 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.3332 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.5333 | 208 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.6333 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.7333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 865 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23680 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.6 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.05 | 70.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.2 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216.9666 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 218.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372.6666 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 463.3 | 226 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 654.7083 | 47.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 955.5 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 963.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1132.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1202.2666 | 142 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1381.9333 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12110 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.26 | 67.42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 295.2 | 98.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 767.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 323.9166 | 65 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 63 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2398 | 872 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.8333 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.9 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.65 | 157 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.2499 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 209.9332 | 188 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 281.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 353.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 484.6333 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 579.7 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 634.4 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 737.1 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 832 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1136.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1440 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2557.5 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2893.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4437.0833 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.25 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.075 | 21.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.7998 | 372 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.6666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.8166 | 151 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176.75 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 513.6666 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 866.25 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 960.4998 | 255 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1600.5 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1917.5166 | 103 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2785.4166 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4555 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4599 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.65 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 148 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 208.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 290.4055 | 43.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 330 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 466.6665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 612 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 743.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1229.6666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2224.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2494.2666 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.4046 | 115.42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 156.99 | 52.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.01 | 44.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 366.6 | 91.65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 604.5 | 120.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1701.98 | 121.57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4529.2333 | 47 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.55 | 51 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 465.075 | 58.5 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2424.84 | 110.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.3332 | 134 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 203 | 58 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2954.0999 | 387 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 434.6 | 164 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 703.58 | 76.2 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.7116 | 54.61 | 1 | 1 | 0342-Pulverizer inert system | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.75 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.5 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.75 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5288.8333 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 693 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2721.25 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92.2667 | 17.3 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 186.8333 | 95 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 992.25 | 135 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1411.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2273.375 | 69.95 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2774.4 | 68 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6667 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10767.5 | 295 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.75 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1705.6666 | 43 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.41 | 24.3 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2563.4166 | 95 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.25 | 45 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6317.4165 | 205 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.5 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 288.0313 | 112.22 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1122.3333 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3017.8333 | 38 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49 | 42 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 680 | 85 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20682.75 | 115 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8635.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 337.2833 | 59 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 401.3333 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.9333 | 68.32 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.4 | 13 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3522.5999 | 108 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146.6666 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2334.9 | 129 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 538.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51 | 85 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.225 | 50.89 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 326.5666 | 101 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 867.1666 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.45 | 149 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2070 | 460 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1008 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280 | 35 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 630 | 70 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1018.3333 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.4999 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 429 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3291.25 | 75 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4174.6666 | 80 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3715.1 | 194 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 392 | 98 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 486.6666 | 146 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 800 | 320 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3574 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.6667 | 20 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 514.25 | 121 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2397.75 | 115 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1857.2666 | 52 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2256.75 | 85 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8505.2499 | 195 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1487.75 | 55 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2663.4 | 36 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 935 | 170 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1125 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2137.4666 | 68 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 558 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 172 | 43 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1037.1333 | 47 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1795.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2788.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31771.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 28294.3333 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 358.1332 | 158 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 756 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13581.55 | 129 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.7 | 31 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.5333 | 52 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3876.6 | 71 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5772.4333 | 71.5 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2576.1 | 62 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2669.5 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16970 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1153.9999 | 120 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163 | 163 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 490 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8721.3333 | 124 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.8332 | 125 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4830.1768 | 72.29 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2682.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 210 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 264.45 | 123 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 803.2499 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1093.3331 | 410 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1652.6333 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.6667 | 5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 211 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 325.4166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2320.4999 | 126 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.3 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 479.9183 | 57.02 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.0833 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.6 | 76 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 155.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.5 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126.6665 | 190 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.5666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 258.3667 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 164.2666 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.1666 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.637 | 53.22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 341.8333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3176.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 246 | 123 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 595 | 297.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.2667 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.05 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.5 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.4333 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.6 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 115 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.1666 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.55 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 168.1 | 82 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60.95 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.75 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.2 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 200.6 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 220 | 200 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 614.9 | 33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.1667 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3471.9 | 163 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3213.15 | 93 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.6 | 34.2 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.1775 | 50.61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 834.5 | 166.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.0833 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.5 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.1666 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.2666 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.4666 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.4666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1393.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.4999 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.9166 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.1333 | 26 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.9999 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.45 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.8333 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 153.85 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3256.25 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.75 | 5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 224.25 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.6666 | 175 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 652.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35.3333 | 106 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 215.7999 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 322.4 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 896 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1253.3 | 151 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.4 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 576 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.8 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.2 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.9166 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77 | 77 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 184.0833 | 235 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.6666 | 245 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.4 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 224.25 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 240 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.9833 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.1333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.1666 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 780 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1769 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.8666 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 101.4 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.74 | 30.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 604.0656 | 58.27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.4 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.4666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.1666 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.4 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.3333 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.25 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 108.8 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 137.6666 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171.45 | 57.15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 387.9333 | 92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 660 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.55 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.5833 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.232 | 72.79 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 351.8513 | 54.41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 552.5 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.9 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.9333 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.5666 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.6166 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 132.75 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 551.65 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.7 | 33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 217.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54.6 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 66.15 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.7333 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 165.2666 | 134 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.8666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 617.5 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.6666 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98.7499 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340.6666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1256.2666 | 112 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267.371 | 122.46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 602 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.5 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.9 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.75 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 329.1665 | 250 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 361 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 785.7333 | 142 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.3666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.3333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 130.2 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2810.738 | 49.88 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 169.7067 | 47.36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.2833 | 101 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.8 | 152 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.6166 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 580.8 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1652.8333 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 275.65 | 111 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 916.5 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.8 | 99 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 950 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.4 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.7333 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.2 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 289.0666 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43.9166 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.0666 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.75 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126.6666 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 508 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.9333 | 52.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2581 | 116 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 203.3333 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.2 | 9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.5 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201.5 | 26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274.5 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.75 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 779.9999 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1327 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.8667 | 26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114.9167 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.8 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 814 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2381.52 | 99.23 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.8 | 3.3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47775 | 245 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.8333 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 427.1666 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 550.25 | 71 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 741 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 799 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2334 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 24 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.75 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.75 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 279.5 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 320 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 794.6666 | 320 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 370.3333 | 202 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1822 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1181.4833 | 91 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 906.96 | 75.58 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 176.39 | 176.39 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 269.16 | 67.29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.4999 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 392.9999 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 395.7 | 79.14 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.2 | 18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.4666 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1078 | 220 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.4 | 69 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.1667 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 240 | 48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.9 | 69 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.8333 | 26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.6667 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 296.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 522.75 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2780.3333 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 387.99 | 129.33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 509.7833 | 73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124.23 | 124.23 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 223.26 | 74.42 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1099.26 | 122.14 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 382.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1019.52 | 254.88 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 133.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 788.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 731.25 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.2 | 66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.6666 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.1666 | 62 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 305.2 | 109 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 641.9999 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 736.6666 | 170 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1002.1666 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2288.2999 | 294 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12 | 18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.85 | 63 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6417.75 | 129 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222 | 55.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 454.02 | 75.67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 299.76 | 74.94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 761.2178 | 105.97 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 607.15 | 121.43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 391.3067 | 8.8 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11402.0315 | 216.7 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.25 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 165.6 | 184 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.3333 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 535.3333 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13963.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4947.8666 | 86 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.6 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.1333 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 430.16 | 107.54 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 514.98 | 57.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 440.24 | 110.06 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 496.32 | 165.44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2033.02 | 184.82 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 5.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1924 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9166 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250.1 | 61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.25 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 370 | 111 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 453.3333 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.9 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.2333 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25.3499 | 117 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.1333 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 704.25 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2341.3333 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 460.68 | 115.17 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 695.68 | 86.96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 438.6733 | 90.76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3103.5 | 206.9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 331.4667 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.3455 | 36.29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.6 | 15.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.3332 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.5 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1912.6666 | 152 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15898.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.5333 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 142.5 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.5 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 665.1666 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1020 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.2667 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.1167 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1612.5 | 258 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 363 | 90.75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 555 | 555 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 271.9999 | 240 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 762.6666 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 72202.05 | 711 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.6666 | 56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.6667 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237.4166 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 314.9999 | 108 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 468 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3623.9999 | 180 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231 | 66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 475 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 781 | 71 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3915 | 116 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4729.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400.5 | 6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 620 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5140.0999 | 294 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 428 | 85.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 625.35 | 125.07 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137 | 68.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.17 | 59.39 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 269 | 134.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 2 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 504.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1929.984 | 50.26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1075 | 215 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 190.6666 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 401.3332 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 421.75 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.05 | 23 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 752 | 30 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 112.8 | 144 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5017.0664 | 818 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 92.9999 | 180 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 35.75 | 65 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 29.9999 | 180 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39.9999 | 96 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 40.5 | 270 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 17.3333 | 65 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 6.5 | 130 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 72.075 | 27.9 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 100 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6698.9998 | 630 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198 | 66 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 33.9999 | 255 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 624 | 72 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 80 | 200 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 14.0833 | 65 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 6480 | 4.5 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798.7498 | 675 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4788.3 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 56.7333 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 131.9999 | 180 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 258 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10564.3164 | 457 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2007.5 | 110 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3003 | 420 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1918 | 685 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 360.4 | 106 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.9499 | 81 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1062.4999 | 102 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2583 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 47.5 | 190 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 312.5 | 250 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 223.3332 | 200 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 78.6 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 387.4831 | 347 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 407 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 729.5995 | 684 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1130.6832 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 7.1666 | 86 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 110.5 | 170 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1000.9997 | 462 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2986.2 | 108 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 112.6666 | 169 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 613.8332 | 254 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 919.3499 | 243 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7546 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 92.4665 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 751.6666 | 110 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6720 | 96 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1077.5 | 431 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6.5497 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 130.9999 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 770.5 | 230 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2955 | 300 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 746.1665 | 605 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 150 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 157.5 | 210 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5634.9332 | 176 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 23.1 | 66 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 245.9999 | 180 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 13.805 | 75.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 1471.625 | 30.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1482.25 | 385 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3735.333 | 431 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 951.4999 | 330 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4689.7999 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 270.6665 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2533.2998 | 462 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1996.9665 | 431 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 307.8499 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 4693 | 76 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1678.3333 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 36 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 427.0833 | 205 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 270.4 | 104 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 641.6665 | 500 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2969.8999 | 102 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4171.5831 | 565 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 446.6667 | 20 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 657 | 39.42 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 105.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 254.9999 | 180 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 495.9 | 342 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2541.7997 | 426 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 25059.4167 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 7099.6665 | 380 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 551.8332 | 385 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 156.7883 | 105.7 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 379.5666 | 118 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1756.8332 | 254 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 1361.6666 | 100 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 650-Fluidized Bed
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 418 | 418 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 419.05 | 493 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1715.9997 | 468 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1070.533 | 518 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 30.0667 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 53.5333 | 11 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 32432.8 | 24 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1.8867 | 22.64 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 219.5833 | 31 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 8.3333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 30.805 | 10.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 114.31 | 42.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2853.04 | 45.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 564.9 | 269 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 104398.5 | 79 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 23.4333 | 37 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 460.7166 | 77 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 3319.2999 | 114 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.45 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 876.3999 | 187.8 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 2277.9166 | 55 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 21.3333 | 2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 3.45 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 941.3333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.1 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 51.75 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 3410.4 | 58 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 34.95 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5137.9166 | 55 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16.25 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 38.25 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 2.8499 | 171 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2879.3333 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 150 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 33.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 45 | 18 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 51.9 | 18 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 578 | 68 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3791.3941 | 106.85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6.2 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 12.9 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 557.7333 | 178 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 20.75 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 80.7 | 107.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 152.6917 | 25.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 58.25 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 428.9978 | 104.21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2473.0125 | 94.21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 355.9665 | 181 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 147.2 | 69 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 123.74 | 107.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 543.25 | 53 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 63.75 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 137.7 | 27 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 369.9332 | 179 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 387.8311 | 94.21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 90 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 378.9333 | 81.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 53.3333 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 61.8333 | 26.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 18.69 | 26.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 32.4 | 27 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 27.0833 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 86.25 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1375.3166 | 179 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 3106.4 | 33 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 70 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 234 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2016 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 2049.6 | 84 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 10.5333 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 206.7 | 39 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 433.9999 | 210 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 860-Co-generator Block
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 11998.3333 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.6667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 565 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1386 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.25 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.1332 | 236 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18792 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.3998 | 339 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.6383 | 74.42 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 5888.1332 | 158 | 1 | 1 | 0360-Burners | U3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 336 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 45.9333 | 106 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 823.3333 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.8 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.8333 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140108.3332 | 430 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 528.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.8 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1656.6666 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 801.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4032 | 168 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.732 | 124.33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3954.1667 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 348.45 | 9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.5333 | 22 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.1666 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.6999 | 102 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 397.9624 | 154.05 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414.1667 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 39.8666 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.7333 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 438.8101 | 121.33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 506 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4100.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.3333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1358.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1590.4499 | 207 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1594.8333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4554 | 207 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 968.6666 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7.6667 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 35 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 42.6666 | 64 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.495 | 144.33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 256.6666 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 534.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2620.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3301.6666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.4666 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345.4405 | 160.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435.2833 | 91 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.2 | 49.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 29.333 | 440 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.6666 | 49 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.8 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 769.7333 | 92 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5860.8333 | 130 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14400 | 240 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.4666 | 108.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.5 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 204.6693 | 65.32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268.3333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.5 | 71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23694.8 | 74 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5868.8 | 44.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1395.6331 | 562 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.3 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.6667 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 923.8333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150.75 | 27 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1879.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 896.2667 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4129.3333 | 190 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 241.8 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 104398.5 | 79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 32432.8 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 9.855 | 8.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 14.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.66 | 15.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 13.3833 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 387.5 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 70 | 42 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 872.9167 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 31.5383 | 12.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1935.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 132.0293 | 51.44 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1121.175 | 7.55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 242.1867 | 23.9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 285.6 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 26559.625 | 142.5 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 60 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4.75 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 590 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2582.8666 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 23.8333 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 814.6666 | 94 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 184.5667 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 148.2833 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4382.4667 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 26 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 25.2 | 13.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 208.3333 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 193.5 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 79.8 | 63 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 91342.4666 | 137 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 862-CoG steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 100103.4667 | 32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 862-CoG steam units
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 359.142 | 20.12 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 5967.5499 | 213 | 1 | 1 | 0366-Duct burners (FBC only) | U1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 6141.8216 | 292.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1337.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 734.5 | 565 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.2 | 108 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 223.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 479.4166 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 139 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.42 | 53.21 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 652.0202 | 235.67 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 545.9664 | 327.58 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 200 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1184 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 63.0966 | 82.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 564.6666 | 110 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.9595 | 64.49 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18093 | 740 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 524.4 | 552 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1523.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 874 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2412 | 134 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1278.9 | 182.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 56.32 | 76.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1375.9165 | 395 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 319.2166 | 107 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 573.9165 | 485 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 473.6666 | 290 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2174.6661 | 815.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.3909 | 181.38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.1666 | 115 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.6166 | 31 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9480.2 | 354.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9211.5 | 230 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.6666 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 10.1967 | 16.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 31421.345 | 292.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1054.9331 | 344 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4686.6664 | 740 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6006 | 858 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 27.87 | 557.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.5 | 150 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 850 | 170 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 988.8333 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 135.8299 | 86.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 53.8917 | 14.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1038.6665 | 380 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.7499 | 339 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7760.8331 | 670 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 139.1999 | 144 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.6666 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 451.6166 | 49 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2694.9997 | 420 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3429 | 635 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5700 | 228 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 684 | 144 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 69.6667 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 292 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 567.2665 | 268 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1666.233 | 518 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 36.4167 | 19 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 404.25 | 147 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 115.02 | 57.51 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 699.567 | 80.41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 35.3333 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 96 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 213.64 | 19.6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 691.6 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 14.6666 | 176 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 50 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 8.3 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 13.5 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 4.3333 | 13 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 14.5833 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 114.1667 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 22666.2 | 37 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 11.7332 | 176 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 127.4 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 469.5833 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 20.5332 | 176 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3128 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 313.1333 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 27.4833 | 97 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 133.3333 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 436.8 | 84 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 12.25 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 2 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 18.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 277.2 | 72 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 39.6333 | 29 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 79.95 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 240.3 | 89 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 504 | 168 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1602.3626 | 45.76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 12.6666 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 87.3 | 97 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 399.2799 | 130.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 54.4 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 3.8 | 6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 5 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 98.3333 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 222 | 37 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 19.6208 | 47.09 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 174.8167 | 17 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 9.24 | 50.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 136.25 | 32.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 12.8333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 34 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4.6667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 54 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 56.25 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 2.6667 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 30.0833 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 118.3333 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 3.5 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 860-Co-generator Block
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 448.2 | 81 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 860-Co-generator Block
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 1239.38 | 59.97 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 861-CoG GT units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79 | 79 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.3333 | 85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 336 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424.3332 | 134 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 302 | 302 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 715.3166 | 257 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679.7775 | 287.23 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D3-Forced - Postponed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3906 | 126 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 466.6665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 650.1333 | 106 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 241 | 482 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.5 | 15 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.7166 | 113 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1358.9162 | 709 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.8833 | 157 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.3332 | 215 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 30533.7 | 102 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D3-Forced - Postponed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4009.5 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 714.9999 | 165 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 52.8 | 18 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.0333 | 53 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 694.8 | 38.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1679.1665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 598.893 | 466.67 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8400 | 750 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.4666 | 104 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.6666 | 140 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3890.3333 | 220 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0166 | 71 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 868.2497 | 453 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43.46 | 21.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.3333 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.4665 | 184 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 888.5399 | 212.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 822.9497 | 453 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.5333 | 82 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30 | 30 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2032.5 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 138.6666 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 134.824 | 70.96 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 50.6666 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 816.6665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1136.6666 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 570.1666 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 326.1665 | 515 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405.5663 | 529 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 197 | 197 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 724.2664 | 448 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.3332 | 132.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.6 | 32 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1241.9916 | 79.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 126.8999 | 81 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1449.0664 | 352 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1598.3331 | 700 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1374.0998 | 453 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 158.5666 | 142 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 500.2665 | 268 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1571.2665 | 518 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 118.3333 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 29.75 | 7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 115 | 230 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 126.5 | 230 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 54.1333 | 14 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 7 | 14 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 59.9133 | 3.8 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 192.405 | 38.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 6.9333 | 3.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 123.6666 | 140 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Winter | 236.5333 | 3.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 281.1 | 18 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 3606.6667 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Summer | 66.22 | 4.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | SERC | Summer | 278.3 | 46 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1088.4999 | 210 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Summer | 51.3333 | 88 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | SERC | Summer | 359.5166 | 37 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 200.6665 | 280 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Summer | 220.5 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 300 | 150 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 861 | CoG GT units | SERC | Winter | 246.6666 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 861-CoG GT units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Gas | GG | 861 | CoG GT units | SERC | Winter | 135 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U2-Forced - Delayed | 861-CoG GT units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.7 | 138 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.759 | 94.61 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 797.9167 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.125 | 59.55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1143.2665 | 311.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 15.1667 | 35 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 716.75 | 235 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2131.25 | 275 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1336.3331 | 380 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 275 | 110 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.3498 | 279 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.3417 | 28.55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.6092 | 28.55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 421.6331 | 278 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 698.54 | 131.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6557.5 | 430 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.3333 | 85 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 770.25 | 195 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 108 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.05 | 19 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.3333 | 14 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.8333 | 98 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162 | 40.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243.1 | 143 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1475.9333 | 4 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 994 | 71 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.6666 | 305 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1057 | 151 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 2 | 3 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123 | 18 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.61 | 46.1 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.9 | 38 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.5 | 90 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 660 | 110 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.5 | 230 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2448 | 90 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 319.6999 | 166.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 930 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 379.9998 | 600 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 37282.9833 | 181 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310 | 155 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134.7166 | 59 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.9067 | 36.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.7332 | 248 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6432.0765 | 351.8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 81.4667 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 302.8332 | 158 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7801.89 | 190.29 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.6664 | 385 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1830.1665 | 395 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 877.6999 | 402 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.4 | 68 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.0016 | 86.9 | 1 | 1 | 0385-Igniters | D3-Forced - Postponed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 463.0389 | 190.29 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1593 | 708 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39 | 45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.9999 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172.3332 | 188 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 568.8833 | 107 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 79.8 | 63 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.1332 | 272 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 107.0333 | 38 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 625 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 33 | 1.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1010.24 | 46.2 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 201.4667 | 4 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2204.6832 | 179 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 81.6666 | 100 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 861-CoG GT units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 11408.0164 | 427 | 1 | 1 | 0390-Burner wind boxes and dampers | SF-Startup Failure | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209 | 19 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 437.784 | 128.76 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.5666 | 106 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16617.4164 | 427 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1117.5 | 149 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 205.4 | 158 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 205.8333 | 19 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 333.35 | 113 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 359.25 | 479 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221 | 130 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 711.4665 | 368 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.5 | 65 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 381.3333 | 65 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209.0666 | 98 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 316.8 | 26.4 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9900 | 330 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10703 | 278 | 1 | 1 | 0400-Burner wind box fires | U2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2629.1332 | 349 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 5147 | 60 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.4 | 2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 80.6833 | 23.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 24 | 22.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 41.4967 | 21.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 112.1833 | 26.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 6 | 3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.6165 | 431 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.25 | 3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 343.3333 | 103 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 129 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 19.89 | 15.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 342.0133 | 22.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 18.6333 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 35.75 | 16.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 45.475 | 25.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 94 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9955.1662 | 742 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Winter | 2389.7499 | 165 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2466 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.2167 | 19 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 37.7067 | 11.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 31.31 | 20.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 172.9833 | 19.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.1666 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 491.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 8.6 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 10.1967 | 16.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 12.8417 | 11.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 36.9417 | 6.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 84.63 | 18.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 124.425 | 13.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 26.52 | 15.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 53.8667 | 20.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 16.0333 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 96.9833 | 23 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 26.6667 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 5 | 1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.1 | 42 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 606.7666 | 167 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.81 | 14.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 40.3 | 18.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 105.6 | 26.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 68 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.1666 | 170 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1312.5 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 5.2417 | 8.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 8.1067 | 12.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 10.8 | 13.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 31.755 | 21.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 39.7267 | 20.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 90.415 | 16.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 793.25 | 167 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 251.4667 | 20.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 14.2 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 21.21 | 20.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 33.8833 | 9.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 160.965 | 21.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 284.0133 | 13.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 29.0117 | 16.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 75.2 | 23.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 91.4333 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 244.6833 | 26.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 12 | 60 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 371.7333 | 68 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1440.8333 | 130 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 4.0333 | 5.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 20.7833 | 14.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 21.4583 | 10.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 37.5417 | 8.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 72.05 | 16.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 42.4233 | 17.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 58.2667 | 23 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 10 | 2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 5.55 | 9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 799.2166 | 79 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1603.2 | 144 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 0.64 | 3.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 43.5 | 29 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 35.7 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 533.1667 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 45 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 118.8 | 8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 22.5333 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 267 | 89 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 118.7465 | 44.81 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 97.0333 | 82 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 985.9333 | 92 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 136 | 85 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 131.9499 | 87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2024 | 92 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 36.9 | 27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 267.4 | 84 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 861-CoG GT units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.4 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.1666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.5833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.0667 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.1 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 12.3666 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.9999 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.5166 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.7499 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 58.3332 | 140 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 96 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 194 | 24 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.35 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 405.1333 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1126.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1533.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 38.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39.6333 | 82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.4 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.4066 | 26.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 491.1667 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2881.4999 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2655.3333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3493.3331 | 320 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1464.12 | 49.8 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3605 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.6667 | 24.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24 | 72 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.3333 | 94 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1009.05 | 93 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1646 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.565 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.2 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.35 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.6666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.9167 | 17 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 152.7333 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 174.3 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 178.8333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 218.8333 | 101 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 553.5 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 965.7333 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3553.5666 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.2666 | 68 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.6333 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 533 | 82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 553.3333 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 770 | 77 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7622.0833 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.3333 | 100 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.25 | 99 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 363.95 | 50.2 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15.4166 | 37 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.95 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 108.2833 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1851 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5376.15 | 117 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.9 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.7 | 66 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.35 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.0333 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.1833 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.8333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.6833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1268.5 | 215 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.2825 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.762 | 5.13 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 322.5 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1338.75 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.7653 | 48.46 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632.4156 | 74.99 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3085 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.0666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 259.5833 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 606 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 792 | 72 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 954.1 | 94 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1507.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3312.5 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3825 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5040 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.5999 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.7333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.3333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.5 | 61 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.3333 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.8666 | 166 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.9 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.05 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.7667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 303.3333 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 320.0785 | 58.73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 343.8 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.2 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1121.6833 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1479.1666 | 125 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1584 | 176 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3402 | 189 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4983 | 151 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.736 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 149.5 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 438.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 811.9999 | 174 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1289.6665 | 292 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112 | 84 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.1716 | 45.85 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.3333 | 160 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.68 | 26.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.4 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.08 | 22.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88 | 17.6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4059.9166 | 215 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.1333 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.5 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.8 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.7 | 66 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.7833 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 430.65 | 99 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 620.5332 | 179 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 968.3333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1443 | 111 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2756.8333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2912.3999 | 216 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.4 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.3333 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 308 | 19.25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 512.5 | 82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6775 | 542 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27254.3333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 4.4 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.4999 | 81 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200.1333 | 79 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.7578 | 68.83 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.4795 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.9925 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.7 | 26.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.2333 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 244.9999 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 544 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.35 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.6666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.95 | 77 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.4715 | 32.83 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.542 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43.0833 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.55 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.5 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.3 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.9 | 66 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 204.0833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.5 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1002.7333 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1472.5 | 93 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134300.5666 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19 | 9.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 614.4166 | 73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 50.05 | 77 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105 | 84 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3.04 | 22.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.9 | 39.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36 | 72 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 114.2166 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 135 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1726.2 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6132 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7333 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.8666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.6 | 3 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.35 | 7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.2 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.0999 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.7 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.3 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.3 | 57 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.6666 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.0499 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.65 | 3 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.9166 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.8167 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.75 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 378.25 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 670.8167 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1200 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1436.9499 | 87 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1579.2 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1895.05 | 151 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2041.2 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2225 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2706 | 123 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.684 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 364.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 444 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1443.75 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.7666 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.0333 | 50.2 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.0462 | 41.51 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.99116 | 3.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.2 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24.2666 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78 | 78 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.3167 | 23.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.8333 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 129.05 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.0333 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1098.4 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4437 | 170 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.394 | 5.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5.4166 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.6 | 62 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.75 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.25 | 57 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.1666 | 106 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 214.3167 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 217.25 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 561.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.3333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.6666 | 82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.7 | 82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1920 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.2 | 72 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38 | 114 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72 | 72 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.48 | 41.52 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 68.25 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 92.75 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 144 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 156 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 120.35 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 96 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 160.7666 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 114 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 236.25 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 168 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 31.4167 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 88.6667 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 95 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 102.9167 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3384 | 47 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1482.8333 | 41 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 329 | 47 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 35 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 405 | 45 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40 | 40 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6790 | 40 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7.2 | 36 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3941.25 | 75 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 291 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.5 | 45 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1090 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 984.1667 | 10 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 78.75 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 888 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3989.8333 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7886.2666 | 88 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 283.25 | 15 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 703.2333 | 73 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 882 | 72 | 1 | 1 | 0425-Cyclone dampers | D3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2081.9167 | 35 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.20717 | 1.13 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 215.8333 | 37 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60403.9 | 334 | 1 | 1 | 0425-Cyclone dampers | U3-Forced - Postponed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 120.75 | 63 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 50 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 344.25 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1163.4 | 42 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1330 | 60 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.6666 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 522.6666 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.75 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 232.3333 | 85 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 71.25 | 45 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 8.75 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.5 | 45 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.5 | 30 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 289.5333 | 43 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1477.3 | 34 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2900.7 | 66 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 776.6667 | 20 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3321.6667 | 50 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6060.5 | 46 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.4283 | 41.51 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1007 | 57 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287 | 143.5 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3638 | 30 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 70.2 | 27 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3250.6833 | 77 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11396.8329 | 590 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19537.8333 | 110 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.0166 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.1999 | 78 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.9333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.5 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.2 | 78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.3333 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.3999 | 78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 733.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.4 | 36 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0833 | 35 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.2 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.75 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.1 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.7 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8667 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.0666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 7.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.2333 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 257.6 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1858.5 | 59 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 28.35 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1544.4 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 667.3333 | 220 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2736 | 320 | 1 | 1 | 0435-Other cyclone problems | SF-Startup Failure | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3434.8852 | 137.03 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.4167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.25 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.6666 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.15 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.7 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.0999 | 78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 5.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.7 | 78 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.9 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.9999 | 108 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.3999 | 78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4224 | 64 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.9 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.8166 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.75 | 27 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.2667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.3667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.3 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.4 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6666 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41 | 20.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 37.8 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.6666 | 40 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.9 | 78 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.7333 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2406 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.1667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.0666 | 31 | 2 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.7333 | 41 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.1667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.7833 | 73 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.85 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.75 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.3333 | 80 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 40 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.1 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.7833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.8 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.25 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.25 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.9999 | 237 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 518.8666 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.5 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.0333 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.1 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4667 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.85 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 11 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.0333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.8 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72716 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 40 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 40 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6666 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 27.3 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3080 | 160 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8666 | 43 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5833 | 43 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.45 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.8833 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.6166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 423 | 105.75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.0333 | 31 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.7333 | 26 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5833 | 31 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.9167 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6166 | 31 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1333 | 31 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.2 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.1 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.9 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.6666 | 40 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 143.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14.7 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 312.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.05 | 41 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.15 | 43 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.4 | 36 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.4667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6 | 66 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.0333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.4 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.3999 | 78 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9335.0833 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.5 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.2 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.2333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.8 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.6 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.4833 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 372 | 62 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 871.2 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.5 | 155 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 381.2166 | 89 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 144.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 403.1 | 87 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 29.1667 | 50 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64736.2663 | 496 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.7333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.4 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3999 | 96 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.0833 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.2 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.4 | 78 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 120 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.2 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.1833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.99999 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.55 | 31 | 2 | 23 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 35 | 1 | 11 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1667 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.0667 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.3667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2 | 41 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.3 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.2833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.4 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 413 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.4166 | 155 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.5166 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 253.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10333.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 326.2166 | 37 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11246.824 | 71.88 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19 | 9.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.6666 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86.8998 | 237 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8 | 36 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.3333 | 35 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.9333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.2166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.4 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.2 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.2833 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6.3 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 34.65 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 302.0833 | 125 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 984 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5238.333 | 449 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1421.2 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 30.8 | 66 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 109 | 109 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 32.5 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 41.6 | 104 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1293.6 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 298 | 149 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 207 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1104.3667 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 727.7498 | 615 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3.2 | 48 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 500.5 | 14.3 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 851-CC GT units
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3402 | 126 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 103 | 60 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2023.1663 | 610 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.6666 | 58 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 11.3 | 113 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 327.0665 | 223 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.5 | 219 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 12.1 | 33 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 283.4832 | 233 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 427 | 20 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330.433 | 431 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 115.9999 | 120 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.8333 | 22 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 45.3333 | 68 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.3333 | 8 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8820.5 | 590 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189.3165 | 307 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 94 | 120 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7273.9331 | 308 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 11.6666 | 100 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 314 | 40 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 437.5 | 175 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 44.7 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.098 | 71.88 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.324 | 71.88 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 291.3996 | 564 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2106 | 108 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56.9333 | 56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 396.5933 | 117.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 796.4 | 33 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 22 | 220 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 28 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 201.5 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91.4666 | 56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.7166 | 119 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61 | 61 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 93.1 | 147 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 53 | 106 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 479.4 | 102 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1759.3333 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 149.3332 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2193 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4048.1833 | 11 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4072.25 | 455 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.6 | 42 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15.3833 | 71 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 270.9 | 258 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 680.4 | 108 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3033.6665 | 380 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 812.82 | 117.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 40 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1127.5 | 410 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 13.3333 | 100 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 51.5666 | 182 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 80 | 320 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 507.6 | 24 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 311.6666 | 110 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.79 | 71.88 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3964.5998 | 258 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 22963.2 | 552 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 186.3333 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 242.08 | 20.4 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1884 | 48 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 45.9333 | 106 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 679 | 97 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 233.6366 | 117.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 621.55 | 93 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10 | 40 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 13.8333 | 166 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 55.6 | 24 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 61.6666 | 185 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 87.9998 | 330 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 167.8667 | 8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 208 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4718.8167 | 11 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1450 | 25 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 804.6666 | 170 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 53.2 | 56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 258 | 258 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 524.1666 | 170 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 738.2666 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 16.4999 | 198 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 34 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 65 | 65 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 351.6667 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1956 | 48 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1240.9998 | 510 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1594.7 | 431 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 320.1666 | 170 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21452 | 692 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 12.5 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 743.6 | 104 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 8.55 | 5.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 22.8 | 15.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 50.5 | 20.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 1.2 | 1.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 44.4 | 22.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 21.4 | 10.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 158.4 | 13.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.2 | 4.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 447.1 | 26.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 867.9 | 26.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 735.5283 | 22.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 751.2 | 31.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 64.8889 | 114.51 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 326.4666 | 118 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Winter | 285.8333 | 175 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Winter | 245 | 150 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 43.4 | 62 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 172.9167 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 346 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 515.2 | 69 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 639 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1494.5 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1603 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1796.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 65.26 | 100.4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 347.0833 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 578 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 605 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1800 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1023 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1034.25 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6123.3333 | 55 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8610.4 | 150.4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 26928 | 528 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8259.8999 | 198 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.2333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.5 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189.75 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 220.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.4167 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2280 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.15 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.3 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.9333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.2667 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.0833 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.6667 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 347.2 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.25 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 672 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 850.85 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 878.4333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 898.8833 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 931 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 141.9 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 181.1333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 459 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3630 | 220 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.6667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.8333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.35 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.6667 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 236.1667 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.55 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 372.75 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 538.3333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1260 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.2833 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 513 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1301 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.65 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.75 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91.6667 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342.8333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 452.8333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2161.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.3333 | 47 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.2 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.0833 | 43 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 376.5 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 718.75 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 766.6666 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1389.8333 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2059 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 405 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 483 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 575.25 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 729 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 857.5833 | 205 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123131.6665 | 650 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.6667 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.8333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 159.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 174.9333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.8 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 224.7 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 456.5 | 66 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 485.7667 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 658.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 895.8333 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 910 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1045.95 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170 | 17 | 2 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 327.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1059.95 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1231.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1292 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1440 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2074 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2922.7167 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 636.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.1 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.3 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.6667 | 47 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 127.9167 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 209.65 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 251.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 583.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 660.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 735 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 926.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1362.8333 | 37 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.15 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169.7333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.0833 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 178.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213.3333 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 506 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 506.8 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 585 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 620 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 966.6666 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1637.5 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 112 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1139 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1224 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46800 | 650 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5273.5999 | 192 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15943.1664 | 331 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.5333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170.5 | 66 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.5 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 337.75 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.9167 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 412.5 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 555 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 670.9333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1913.9333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.1667 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 227.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 271.25 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 439.1666 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 660 | 33 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1020.8 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 725 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7097 | 151 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10022.0999 | 198 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86811.9991 | 1320 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.4 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1836.0333 | 24.7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.8667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.5 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.25 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 498.75 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 798 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1740 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.75 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.3333 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 424 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.25 | 31 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 427.75 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 442 | 34 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 453.3333 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 455 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.5 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 514.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 527.9167 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 561 | 51 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 927.9667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1110 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1782.8333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4780.75 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.3333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70.3 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.8167 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162.6667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 360 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 468.6667 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1155 | 220 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4891.2496 | 525 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51399.9998 | 750 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18570.1495 | 783 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 580.3833 | 97 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 440.19 | 60.3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 800-Miscellaneous
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3222.9999 | 165 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 5859 | 315 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1254.285 | 309.7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 98 | 105 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 704.4266 | 81.28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3069 | 165 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 345.8333 | 250 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 3792.9 | 269 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 294.9332 | 158 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 11277.5 | 130 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 533.4999 | 165 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 861-CoG GT units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.4 | 1.6 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.1 | 1.7 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8970.2666 | 28 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 390.4 | 12 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374.0333 | 229 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 239.4 | 114 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4609.92 | 24.01 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.2666 | 284 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1181.345 | 251.35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 60 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3998.5 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1395.15 | 393 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 40.3333 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480.96 | 6.68 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 571.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145 | 145 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 13136.9997 | 522 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1205.75 | 455 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17019.34 | 17.42 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.3533 | 2.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480.9665 | 307 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24911 | 580 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7429.8333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 60 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 381.9333 | 68 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 402.5 | 35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 206.3375 | 165.07 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1227.6831 | 619 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 305.0667 | 22 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17671.3332 | 260 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 677408.6 | 734 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11599.8663 | 575.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14744.2931 | 575.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.1 | 1.58 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 340.4 | 2.96 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2189.6 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8099.75 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1464.6667 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 555.3 | 617 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.5 | 1.5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.3333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5723.6667 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27287.1658 | 1330 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4115.88 | 6.66 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5457 | 255 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18742.8266 | 35.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1012.6667 | 39.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.0667 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 336.7 | 21 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 272.01 | 90.67 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.6166 | 32.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5262.9499 | 231 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10048.08 | 358.86 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 82.0167 | 19 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 2573.04 | 107.21 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 223 | 55.75 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 1510 | 151 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 5398.6333 | 119 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170 | 170 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 547.1666 | 70 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2349 | 405 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44314.7499 | 255 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55312.5 | 750 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3643.9999 | 240 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3014.6665 | 560 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 4252.4664 | 454 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 201.1466 | 30.4 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 137.7 | 8.1 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3554.5332 | 424 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 23121.4933 | 150.4 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250.6666 | 80 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39568.4137 | 510.67 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3147.7332 | 454 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129.5667 | 13 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1336.6666 | 200 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8193.9997 | 510 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11284.55 | 839 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16957.5 | 1330 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 143932.9164 | 475 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8519.9999 | 450 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6477.0664 | 454 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 903.4666 | 154 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18983.3331 | 670 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 387.3333 | 83 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3111.75 | 135 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.5 | 30 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 56.8125 | 75.75 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95674.9995 | 750 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1334.6666 | 110 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.8333 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5969.8332 | 245 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12465 | 554 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17095.4663 | 496 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 841.1773 | 73.04 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3024.9999 | 300 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5580 | 300 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 323.4 | 132 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 77.38 | 63.6 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Winter | 1760.4166 | 169 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 6257.235 | 141.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 187.77 | 170.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 277.9999 | 120 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Winter | 77 | 140 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 37.3266 | 279.95 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4087.3516 | 92.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 34.14 | 170.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 65.8833 | 67 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1053 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.1667 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 569.2167 | 41 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.1833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.75 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.8333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.6667 | 22 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.5 | 35 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 325.8332 | 170 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10673.6664 | 710 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20450 | 250 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 318.9333 | 32 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2773.15 | 111 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.66667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.1667 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.7167 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.9833 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 470 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.25 | 27 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1507.9999 | 195 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 27005.1666 | 311 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 344.2333 | 46 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5629.4998 | 243 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5667 | 11 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.75 | 39 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.6833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 621.3 | 57 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1115.4 | 39 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4440 | 80 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45505.2664 | 758 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9294.75 | 405 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 1.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.8667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1771 | 161 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.25 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 20 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.2 | 26 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.5 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 522.5 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 521.3332 | 340 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1453.8664 | 752 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1215 | 50 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.1333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.6667 | 20 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228.6667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 646.8 | 22 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 677.6 | 28 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1192 | 120 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5110.9996 | 570 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.0833 | 29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1661 | 151 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10057.5 | 450 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 427 | 61 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.75 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.9333 | 34 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.45 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.5667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.3333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 318.5 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 992.3667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.2 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.5 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.25 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.5 | 26 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1127.4 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1378 | 520 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7257.9998 | 570 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 254.1 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 945.5 | 310 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3229.5999 | 132 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10096.083 | 485 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96832.4998 | 450 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2462.4 | 76.95 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.1667 | 26 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.4333 | 29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.7 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301.4666 | 28 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 929.1 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1967.1333 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131085.5 | 871 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29965.8328 | 770 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 66027.1498 | 243 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 11202.4999 | 75 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 8687.25 | 429 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 5484.2665 | 226 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4575.55 | 769 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2714.4332 | 242 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 100.6666 | 151 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1333.4 | 118 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Winter | 2572.5 | 147 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22857.6 | 192 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12564.6665 | 470 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 48103.2 | 393 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9219.6664 | 340 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3189.3333 | 160 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11919.6532 | 354.4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6303.3332 | 200 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7491.3332 | 340 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668 | 167 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 7920.4999 | 186 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 699306.4665 | 542 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 17685.4999 | 186 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25916.3331 | 580 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 65455.533 | 542 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 20195.8332 | 250 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 466.7164 | 683 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 43120 | 308 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 375.6 | 187.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 10482.8083 | 156.85 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 7057.7 | 178 | 2 | 2 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 10645.8816 | 159.29 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1779.125 | 165.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5828.6 | 151 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 22247.5166 | 161 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 601.25 | 162.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 18479.7375 | 276.85 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2972.2 | 77 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 7307.5 | 185 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 162.4 | 81.2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 19113 | 138 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 25978.4666 | 188 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36500 | 500 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 142724.4 | 364 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34645 | 130 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39807.049 | 175.13 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 2770.95 | 147 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 10790.7999 | 159 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U3-Forced - Postponed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 2663.1499 | 147 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2168 | 96 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 5627.4 | 83 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U3-Forced - Postponed | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4692 | 255 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | WECC | Winter | 3171.3665 | 178 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 861-CoG GT units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 2084.5499 | 117 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 862-CoG steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252 | 126 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.25 | 45 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3270.8 | 7.4 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280.25 | 19 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.5833 | 25 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 828.2 | 123 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1813.965 | 437.1 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 718.02 | 119.67 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 165 | 33 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15099.5 | 598 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238 | 35 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1716 | 9 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42795 | 634 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3660.25 | 121 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1031.04 | 114.56 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 650-Fluidized Bed
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5154.2999 | 162 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 418.4999 | 162 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 1175.4332 | 179 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 5306.4 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Winter | 631.8332 | 170 | 2 | 2 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 153.3 | 63 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 458.9999 | 162 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 802.4333 | 181 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 32.857 | 11.33 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 858.9395 | 16.63 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5151.6 | 162 | 2 | 2 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6567.7332 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 616.6833 | 163 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 77.8667 | 32 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 10082.9831 | 323 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Summer | 63.1833 | 223 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Summer | 282.9 | 123 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 140.4666 | 98 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 404.95 | 89 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 951.4665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Summer | 118.9333 | 223 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 954.7999 | 186 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 51.62 | 17.8 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 13916.9332 | 248 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 25.825 | 0.5 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 392.9999 | 90 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1753.75 | 575 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1103.1365 | 596.29 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 792.6832 | 239 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 21133.7499 | 165 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 46.2 | 42 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1639.7975 | 596.29 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 11021.4999 | 282 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2077.1666 | 242 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 152.855 | 160.9 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 1615.6666 | 148 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 134.1782 | 164.3 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 91.85 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 470.3832 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 673.6666 | 215 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 202.1396 | 38.02 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 35.7 | 238 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 47.3166 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 387 | 215 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 606.7666 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 322.4 | 248 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 186.4832 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 921.2832 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 300 | 150 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 8.35 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 985.3 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 44.7666 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 205.4665 | 268 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1081.5 | 126 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 577.875 | 22.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 296.1 | 94.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 55.0275 | 10.35 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 170.1 | 94.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 595.4666 | 203 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Winter | 91.4666 | 112 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1235.7666 | 113.2 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 86.9 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 646 | 323 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 10569.9997 | 420 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3144.6999 | 177 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 484.5 | 85 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 32.1167 | 41 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 257.55 | 101 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 2090 | 152 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2064.21 | 165.8 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 856.8 | 153 | 2 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 534.65 | 125.8 | 2 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 84.3333 | 110 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 365.25 | 146.1 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 6999.75 | 153 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 11096.4 | 168 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 101.6166 | 234.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4427.5 | 322 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 1098.09 | 88.2 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5344 | 167 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 10435.9 | 158 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Winter | 1041.6 | 186 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 889.1 | 209.2 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 4 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 3.6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.3667 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.25 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.45 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.65 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.7333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.0833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.6667 | 38 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8560 | 80 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 4.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.99 | 3.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43 | 10.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29223 | 340 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 3 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.99 | 8.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4283.4999 | 78 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.33333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.55 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.2667 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1445.1333 | 53 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.50417 | 0.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 7.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.0667 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 497 | 10.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6751 | 60 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.75 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.0667 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 921.4 | 68 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 979.2 | 48 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.75 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 114325.5 | 766 | 1 | 1 | 0570-Other reheat steam problems | U2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 5 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148 | 74 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.5 | 18 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.6666 | 28 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 100 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1800 | 120 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3801.6 | 48 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31 | 6.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1138.25 | 157 | 1 | 1 | 0570-Other reheat steam problems | SF-Startup Failure | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2667 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.5333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.98 | 5.07 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 7.5 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176.1417 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3664 | 60 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.05 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.6333 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.8792 | 5.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.5333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 6 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6236 | 60 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.8 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.4 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1620 | 90 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4500.8333 | 50 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 3 | 1 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 6 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.8333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.3833 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 5.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13 | 3.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 41.4296 | 112.99 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 720 | 300 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 726 | 605 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3233.6 | 1376 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 12.2666 | 147.2 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 17.1732 | 147.2 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 8.2042 | 44.75 | 2 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 47.6666 | 260 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31.25 | 125 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 892.9666 | 43 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1072.5 | 71.5 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15093.8664 | 364 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.1666 | 95 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 675 | 180 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 52659.5998 | 504 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3350 | 200 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 284.5 | 113.8 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14196.6 | 594 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22674.3345 | 497.79 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 13999.3333 | 110 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.7499 | 75 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 315 | 140 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.5 | 150 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 80.5 | 115 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3570 | 510 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 350.318 | 65.48 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2757.5332 | 266 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22194 | 274 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1445.7 | 122 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1941.2999 | 162 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13615.4666 | 112 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.75 | 105 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.3816 | 42.7 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.6 | 33.7 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25793.2664 | 842 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1025.7333 | 157 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2548.1498 | 339 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.5333 | 16 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 967.8665 | 244 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 984.2 | 266 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1111.131 | 352.74 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72500.9999 | 180 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1022.8999 | 159 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.32 | 69.92 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1189.9998 | 510 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 37902.4164 | 785 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1966.8999 | 78 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374.4 | 54 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4801.6665 | 268 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2555.5 | 190 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152.8333 | 70 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 606.333 | 428 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 752 | 188 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.6666 | 40 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2171.5 | 430 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 827.2833 | 49 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5842.7999 | 162 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1112 | 278 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12592.7998 | 324 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.9975 | 58.55 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1159.1665 | 214 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 725 | 25 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2665.5999 | 96 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 733.7 | 506 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78289.2499 | 195 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6 | 16 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.7925 | 38.35 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5830.75 | 415 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28637.5 | 395 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9066.75 | 385 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4266.6665 | 250 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1620 | 45 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 52.6167 | 11 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 800-Miscellaneous
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14 | 14 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.1667 | 11 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.2 | 48 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 12 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.6833 | 11 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91 | 13 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.5833 | 11 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64 | 8 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 11 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 222 | 74 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 676.2 | 69 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.25 | 15 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 875.4666 | 134 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.3333 | 13 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462 | 22 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 760 | 19 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.5 | 21 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 859.1 | 121 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 980.5667 | 23 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 610.6667 | 4 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 32.0833 | 55 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 165.8832 | 269 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 20163.64 | 141.4 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3614.9994 | 900 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12316.2997 | 411 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 6059.4166 | 43 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560.2666 | 176 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2008.9333 | 244 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 390 | 195 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 336.2499 | 161.4 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4256.8 | 626 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 656.3666 | 194 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 696.6666 | 88 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 15.4999 | 186 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 26 | 40 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 83.22 | 131.4 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 105.7999 | 138 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 605.9666 | 106 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18424.3329 | 620 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3081 | 474 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7885.733 | 497 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11111.8331 | 290 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 1264.47 | 74.6 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | SF-Startup Failure | 650-Fluidized Bed
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1119.9999 | 336 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37309.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12761.3163 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1879.9329 | 692 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.15 | 33 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9349.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1154 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4216.3332 | 364 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.4163 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30739.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3845.6 | 437 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4381.1 | 454 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76164 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3510.9332 | 454 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1975.6092 | 477.97 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4076.5 | 1315 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2438.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11200.6662 | 634 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3962.0663 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 906.1 | 533 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 36652.9332 | 454 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91056.9996 | 1110 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6227.25 | 437 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18320.1 | 773 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 26791.7998 | 252 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4573.75 | 365.9 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6218.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5708.1666 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1638 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163.4667 | 16 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17842.5 | 650 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 797.4998 | 330 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.3331 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17306.6665 | 590 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23409.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1321.6666 | 305 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16899.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23649.6 | 758 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4277.5 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9752.0831 | 775 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2859.9997 | 429 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 650-Fluidized Bed
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1095.6664 | 692 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2394 | 280 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2312.8 | 413 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | D1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1203.9997 | 840 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8017.0998 | 546 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 787.5 | 750 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 21.975 | 29.3 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 800-Miscellaneous
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 82.41 | 60.3 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 800-Miscellaneous
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 141.6167 | 29.3 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 800-Miscellaneous
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 11427.1666 | 110 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 194.25 | 37 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3690 | 369 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D3-Forced - Postponed | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8344.3996 | 552 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 116.6 | 106 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1665.1996 | 552 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 24385.4666 | 296 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 121.1332 | 158 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 16311.85 | 41 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 158 | 158 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 592.5 | 158 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 5650.4 | 14 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 65.1666 | 85 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | TRE | Winter | 1262.7332 | 188 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 861-CoG GT units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 412.5 | 110 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4509.5 | 58 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2433.6666 | 245 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14600 | 100 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.3332 | 250 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 62 | 60 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2887.1331 | 682 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 174.9583 | 80.75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2691.1125 | 128.25 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 18 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 198.9 | 18 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 866.6665 | 500 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26332.1665 | 271 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7612.3333 | 82 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 43808.85 | 81 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 643.6 | 12 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1609 | 30 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1464.182 | 186.52 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 27.4193 | 74.78 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 8439.9899 | 290.7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1875 | 250 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 14.7913 | 40.34 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1929.9999 | 300 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2599.6332 | 167 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 487.6666 | 154 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 702.2499 | 159 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 706.1665 | 223 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 463.7499 | 105 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2459.5332 | 158 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 48.75 | 195 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10395 | 385 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2718 | 151 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6109.9999 | 195 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 375.8331 | 275 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 586.6666 | 275 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.1333 | 44 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 12326.5558 | 208.63 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | SF-Startup Failure | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5597.425 | 90.5 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | SF-Startup Failure | 852-CC steam units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4332 | 152 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 310.7498 | 339 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 112.5 | 250 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 418.7 | 158 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 421.35 | 159 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 688 | 215 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1285.73 | 127.3 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25538.3332 | 385 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11019 | 90 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 148409.2664 | 412 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98541.6663 | 550 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11100.75 | 615 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 8416.5 | 186 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16666.1665 | 554 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 757.025 | 28.3 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 800-Miscellaneous
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 94.3999 | 177 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.0832 | 125 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102148.6666 | 140 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 58.5 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 33469.0216 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62827.3 | 817 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7368.75 | 15 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1575 | 35 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 666.75 | 95.25 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 19.5 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4358.6666 | 112 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 4120.3666 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 164.8266 | 88.3 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 35343.0899 | 383.4 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2391.9998 | 552 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4645.8666 | 281 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2666.6666 | 100 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3409.15 | 41 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9467.2498 | 585 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184.8666 | 236 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1740 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 51 | 170 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156.5333 | 2 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7750.8016 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1714.3328 | 740 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 532.5598 | 570.6 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7662.3333 | 90.5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 69922.9999 | 84 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 60345.637 | 92.18 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 10 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3504.05 | 69 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 375 | 75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2277 | 15 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 4953.96 | 83.4 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 968.75 | 155 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128458.85 | 107 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10730.4666 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 227.9 | 106 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13506.4999 | 210 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1255.5 | 93 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10800 | 15 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1233.2697 | 383.4 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9407 | 409 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26532 | 670 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 411.25 | 235 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7678.25 | 15 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4870.6 | 85.75 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 76.6666 | 230 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 347.5 | 30 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 4301.6666 | 100 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 624 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 186.3333 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 49.1333 | 26.8 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 862-CoG steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.7 | 51 | 1 | 11 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8 | 54 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.25 | 51 | 1 | 6 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.5 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.35 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99.45 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.25 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 236.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 399.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 409.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 413.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 671.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 686.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 989.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1132.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1219.75 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1003 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6313.3332 | 200 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.75 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.9 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.05 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.35 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 254.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 265.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266.9 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 324.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 470.9 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 500.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 625.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 685.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 850 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 951.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 952.85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 963.05 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1015.2 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1054.85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1167.05 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.55 | 51 | 1 | 24 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.8 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.75 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 272 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 331.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335.7 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 435.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 640.9 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 651.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 935 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 946.05 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 964.75 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 987.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1067.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1079.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 30 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 219.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1080 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.1 | 51 | 1 | 6 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.15 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.35 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 194.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 258.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 273.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.2 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 382.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 510 | 51 | 1 | 3 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 715 | 286 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 721.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 837 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 997.2 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1014.3 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1030.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1073.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1123.7 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1144.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1311.3331 | 281 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17580 | 100 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 489.9999 | 150 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6378.1665 | 539 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.84997 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4 | 51 | 1 | 11 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.6 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.25 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 179.35 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 228.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 279 | 54 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 326.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 334.9 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 340 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 542.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 562.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 703.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 840.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 949.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1093.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1161.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1175.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1188.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1224 | 51 | 1 | 4 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 466.82 | 274.6 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2918.0833 | 95 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5958.3333 | 65 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 1918.3333 | 100 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.1 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.35 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.6 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 304.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 474.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 916.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 952 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 988.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1120.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1147.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.7 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.4 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.2 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176.4 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 212.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 227.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 249.05 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 296.65 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.55 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 746.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 906.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 968.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 977.5 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1008.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1127.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1135.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1154.3 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 204.9298 | 267.3 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 807.177 | 49.98 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 98440.9999 | 294 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 449.55 | 333 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22044.45 | 523 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.9 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.3 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.25 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.15 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.25 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162 | 54 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 224.4 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 232.05 | 51 | 1 | 2 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.6 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 448.8 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 651.95 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 966.45 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 969.85 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 991.1 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1097.35 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2695 | 35 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.7 | 51 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 413.3332 | 200 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2521.2499 | 75 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 18.4167 | 13 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 800-Miscellaneous
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 2535.8666 | 88 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 850-Combined Cycle Block
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 325.5999 | 222 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 851-CC GT units
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 148.8666 | 101.5 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 852-CC steam units
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 20 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2304.5 | 92.18 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122913.2666 | 114.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4073.04 | 14.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 615.96 | 104.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D3-Forced - Postponed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6418.2999 | 318 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | SF-Startup Failure | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2318.4 | 134.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1052.64 | 14.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D3-Forced - Postponed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 13392.2176 | 92.18 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2870.64 | 354.4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | SF-Startup Failure | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 21083.983 | 479 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U3-Forced - Postponed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 16986.4499 | 279 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 130918.7 | 374 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1312.85 | 217 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6343.4166 | 163 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16722.5332 | 266 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7682.15 | 467 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2928.75 | 213 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20954.1331 | 404 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3398.3666 | 269 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 850-Combined Cycle Block
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1037.1666 | 245 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6883.3333 | 70 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2942.3998 | 288 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24462.5 | 515 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6916.8 | 528 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6443 | 340 | 1 | 1 | 0760-Boiler recirculation valves | U3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 460 | 120 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11457.8332 | 427 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1431.3331 | 565 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6136.3996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.9167 | 5 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4952.6665 | 190 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1054.4999 | 342 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 98.85 | 9 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 850-Combined Cycle Block
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3141.3 | 222 | 1 | 1 | 0770-Other boiler recirculation problems | U2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3687.4995 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.7333 | 104 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26512.5 | 750 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1840.1665 | 362 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 165.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 111.8 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 235.0833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 534.7333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 123.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 288.1667 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 234 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 28.3833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 381.3333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 248.0833 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 182 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 897 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 433.3333 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 533 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 988 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 256.5333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 6666.1333 | 232 | 1 | 1 | 0770-Other boiler recirculation problems | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2236.6666 | 55 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15115.833 | 850 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 141.6666 | 100 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1768.7 | 69 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 27236.3331 | 404 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1805 | 19 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5749.0833 | 19 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6156 | 19 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 28761.0499 | 393 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 34368.8333 | 178 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1452 | 144 | 1 | 1 | 0775-Economizer piping | SF-Startup Failure | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 321.9499 | 411 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6317.96 | 49.8 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4851.8332 | 215 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1150 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 2776.4 | 66 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 5588.85 | 58.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 19060.92 | 58.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 23189.7999 | 282 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 11371.95 | 683 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 17800.9775 | 58.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 9248.75 | 245 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 5340.4 | 338 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 1585.5 | 151 | 1 | 1 | 0775-Economizer piping | SF-Startup Failure | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | SERC | Winter | 1213.0333 | 151 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 662779.0832 | 355 | 1 | 1 | 0780-Headers between tube bundles | U3-Forced - Postponed | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23393.3331 | 580 | 1 | 1 | 0780-Headers between tube bundles | U3-Forced - Postponed | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1253114.1332 | 352 | 1 | 1 | 0780-Headers between tube bundles | U3-Forced - Postponed | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 854.9333 | 112 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 152672.3665 | 542 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13934.7 | 78 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U2-Forced - Delayed | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16309.8 | 442 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U2-Forced - Delayed | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 951.5998 | 468 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 15258.6999 | 318 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 850-Combined Cycle Block
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2533.9348 | 290.7 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2605.2 | 78 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7432.3333 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7847.6498 | 249 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2382.9 | 78 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 449.9998 | 270 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 19.95 | 19 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 848.5333 | 68.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1011.9998 | 330 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1774.1 | 157 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 202.6667 | 20 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72781.5829 | 635 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 2332 | 66 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43792.1955 | 746.67 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15963 | 510 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 54830.4164 | 385 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2942.5 | 110 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 394.4 | 58 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 9384.6665 | 280 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 27137.7999 | 282 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | MRO | Winter | 120.75 | 161 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 694.4 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3977 | 164 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 129.9999 | 150 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2710.45 | 151 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2489.6666 | 77 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 957.8666 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 89.2666 | 103 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 52.5 | 70 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4304.0499 | 177 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 392 | 160 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.65 | 179 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 998.2 | 644 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 560.3331 | 336.2 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13494.15 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18623.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 47.2497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4508.5 | 635 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1480 | 370 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 158.1666 | 130 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9101 | 380 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4461.7497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3867.5 | 455 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 587.233 | 446 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189.9999 | 228 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 136.2665 | 292 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 253.929 | 390.66 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 702.3667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 330 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3435.7499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4785.5499 | 363 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17042.6664 | 415 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 383.3295 | 333.33 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375.0666 | 58 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 54.6666 | 80 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.25 | 55 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2033.1497 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.9998 | 342 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2609.1 | 446 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.75 | 431 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 14.25 | 45 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 858.8166 | 227 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 88.4332 | 379 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22188.9 | 222 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 965.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2833.6 | 644 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 475.6999 | 201 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1402.9998 | 690 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1694.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 352 | 120 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4515 | 525 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1069.6 | 112 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 361.8666 | 92 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 800-Miscellaneous
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 53.6333 | 160.9 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 239.9332 | 236 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1271.1666 | 145 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1665.6665 | 190 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 134.4 | 72 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 32.5731 | 279.2 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7035.6 | 492 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 95 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 402.6163 | 493 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2450.5 | 338 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 380.7672 | 164.36 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 70 | 280 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 216 | 216 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 4264.65 | 117 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 584.9332 | 328 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 451.9163 | 493 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1740.7 | 338 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 69.9999 | 168 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 15101.865 | 290.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 392.1999 | 222 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2016 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 11076.3333 | 101 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 15.1 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 142.9166 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 1021.7666 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 176.4 | 168 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 1078.65 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 6277.8499 | 159 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 94.77 | 145.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 84.5466 | 149.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 58.3333 | 70 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Summer | 67.6666 | 116 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11.625 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 7.65 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Summer | 63.8 | 116 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 75.5 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 54.1166 | 191 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 64.1666 | 154 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 11.1999 | 168 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 17 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Winter | 841.9332 | 173 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 941.6667 | 50 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 204.1666 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 26.35 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Winter | 270.8333 | 250 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1108.6332 | 158 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 24.2 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 7.94 | 39.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1098.1 | 158 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 32.7166 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 157.6165 | 193 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 161 | 70 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Summer | 218.7333 | 193 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 15923.5999 | 145.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 19.9891 | 70.55 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 26.9166 | 95 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 76.5225 | 26.85 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1380 | 200 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 17.8273 | 31.46 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 55.1933 | 97.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 749.3333 | 160 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 138 | 138 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 16.545 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 7.615 | 30.46 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 61.8605 | 95.17 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 110.25 | 105 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 115 | 138 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 83.4841 | 70.55 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 41.6666 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 6180.3 | 189 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 51.85 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 47.5 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 153.5166 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 226.2999 | 186 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 120.1332 | 212 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 303.3332 | 260 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 65 | 130 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 89.9999 | 270 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 162.6666 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 422.4 | 256 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 879.6666 | 130 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Winter | 18.1333 | 136 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 54.39 | 54.39 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | SERC | Summer | 1498.3333 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 79 | 79 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 105.6 | 264 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 229.7665 | 226 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 126.0092 | 164.36 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 63 | 105 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 189 | 315 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 441 | 315 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 5801.25 | 105 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 81.6999 | 114 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2738.1332 | 544 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 0.26666 | 16 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 103.0466 | 150.8 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 9538.683 | 183.26 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 275.3332 | 140 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 427.2 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 99.55 | 181 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 35.625 | 142.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 62.4833 | 163 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 92.3666 | 163 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Summer | 2.4349 | 146.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 319.6999 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 53.7355 | 153.53 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 26.8333 | 70 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 2986.43 | 204.55 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 35.925 | 143.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 60.55 | 173 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 186.5665 | 193 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 359.8124 | 172.71 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1231.9833 | 193 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 9.1999 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 90.9332 | 176 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 162.9 | 181 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 164.1666 | 197 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 12.4333 | 149.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 8.1166 | 97.4 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 192.7333 | 98 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 206.5832 | 185 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 42.5179 | 182.22 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 373.9332 | 158 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 60.7399 | 182.22 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 34.3 | 98 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 53.8333 | 95 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 23.4675 | 93.87 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 105 | 126 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 23.2675 | 93.07 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 67.2605 | 98.43 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 33.2615 | 285.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 208.4999 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 259 | 185 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 88.2 | 98 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 68.7166 | 133 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 84 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 20.5013 | 153.76 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 77.024 | 144.42 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 150.2665 | 184 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 110.2499 | 135 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2691.15 | 233 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 153.9 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 100.7 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 32.7166 | 151 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 28.26 | 141.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 104.1846 | 142.07 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 200.4 | 167 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 264.25 | 151 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 40.2666 | 151 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 174.1665 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 273.8233 | 184.6 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 124.6665 | 187 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 78.0046 | 106.37 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 168.1499 | 171 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 37.62 | 51.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 128.88 | 107.4 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 227.5 | 130 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Summer | 207.6666 | 140 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 18.46 | 92.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 120.95 | 123 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 60.6666 | 91 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 87.0833 | 95 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 182 | 280 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 271.35 | 60.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 2608.84 | 179.92 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 288.3 | 18 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54334.4666 | 49 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27546.4999 | 111 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 69025.6667 | 26 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57999.9994 | 870 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11190.6665 | 220 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 900 | 60 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 32.0833 | 175 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.1 | 4.3 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4562.2818 | 68.83 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1586.5 | 334 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69588.4665 | 316 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 68970.9047 | 509.7 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 227.5166 | 73 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.97 | 1.79 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4244.62 | 49.8 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35891.6665 | 250 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6012 | 18 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 991.1665 | 190 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 7877.1932 | 377.2 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3931.2498 | 255 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 90577.6664 | 385 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1636.25 | 55 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.4 | 1.6 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5684.5909 | 262.77 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 122.6666 | 92 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 37041.6666 | 125 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2733.5 | 497 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15456.9999 | 435 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9718.3332 | 245 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3587.7332 | 224 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 532369.7161 | 871 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 255.2999 | 207 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 517.3333 | 80 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 39600 | 330 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1138.02 | 189.67 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1950 | 195 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11142.9998 | 330 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4419.9997 | 510 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 367.6166 | 137 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2815.8332 | 310 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2779.3665 | 199 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.55 | 31.8 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3830.75 | 199 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1215 | 243 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11706.1097 | 509.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 2053.62 | 76.06 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 5421 | 278 | 1 | 1 | 0830-Doors | D3-Forced - Postponed | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 283.5499 | 159 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 623.1999 | 123 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Winter | 858.2774 | 162.45 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13392.65 | 123 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 874.9199 | 165.6 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 12160 | 75 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 1896.3 | 60.2 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 860-Co-generator Block
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 504.6 | 174 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 266.5999 | 186 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 87.4333 | 61 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 391.5 | 135 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2979.5 | 101 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44621.8332 | 158 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12920.3833 | 181 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13899.9664 | 334 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 758.6667 | 8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24174 | 158 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 184.25 | 33 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 58.3 | 33 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 627.2 | 48 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 465.5 | 38 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 298.2933 | 13.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 800-Miscellaneous
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 34.1667 | 10 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 779 | 82 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37188 | 9 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5012.3333 | 44 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 140.2999 | 138 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23577.3998 | 462 | 1 | 1 | 0847-Other expansion joints | U3-Forced - Postponed | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.5 | 46 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7100.0999 | 189 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10578.5999 | 243 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5285.5 | 55 | 1 | 1 | 0847-Other expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16975.3499 | 189 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 31029.6482 | 361.3 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 16492.5532 | 242.3 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1671.25 | 35 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 16272.75 | 117 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 850-Combined Cycle Block
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 36973.8 | 164 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 850-Combined Cycle Block
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1380.6667 | 10 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 780 | 26 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.3333 | 5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1430.5 | 30 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 3406.5383 | 21.7 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 18.99 | 6.33 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 999 | 111 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 42.9 | 14.3 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 2208.92 | 13.72 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 0.98333 | 1 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 7.02 | 1.17 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 18.55 | 21 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 383.75 | 5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 168.56 | 3.01 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 257.75 | 5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 4198.624 | 28.64 | 1 | 1 | 0850-Other internal or structural problems | U2-Forced - Delayed | 100-Fossil-Steam
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | TRE | Winter | 29708.1333 | 181 | 1 | 1 | 0850-Other internal or structural problems | U2-Forced - Delayed | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 764.8667 | 7 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 826 | 12 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 718.3866 | 60.2 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 860-Co-generator Block
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.866 | 116.76 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 713.7231 | 345.35 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2188.6666 | 335 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Winter | 6908.55 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 278.6667 | 44 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.7333 | 44 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.0499 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5058.3333 | 50 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 751.15 | 181 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13030.4998 | 630 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.7667 | 14 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7746.2 | 77 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3969.7 | 21 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 26.4333 | 122 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 25.8 | 172 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1300.9666 | 62 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 53 | 106 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.2 | 69 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 256.2666 | 124 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.3333 | 34 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 659.9333 | 38 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2561 | 60 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 535.5 | 21 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 138.65 | 47 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3822 | 72 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.2666 | 124 | 1 | 2 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.95 | 153 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1223.2666 | 236 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | SF-Startup Failure | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 712.4999 | 225 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 360.9999 | 114 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0858 | LP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Summer | 60.9 | 126 | 1 | 1 | 0858-LP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0858 | LP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 30.6433 | 63.4 | 1 | 1 | 0858-LP Drum relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52986.25 | 485 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 7313.5333 | 44 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126362.8332 | 490 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35382.6664 | 340 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46472.3332 | 340 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121024 | 496 | 1 | 1 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 17276.5099 | 345.3 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 650-Fluidized Bed
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 47542.5999 | 351.3 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 650-Fluidized Bed
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 210 | 30 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 112 | 16 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 30595.7499 | 255 | 2 | 2 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 22346.4999 | 255 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 850-Combined Cycle Block
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.75 | 25 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.3333 | 35 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.1666 | 77 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1767.35 | 39 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35999.64 | 664.2 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | U3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340 | 170 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 581.9466 | 111.2 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122 | 61 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2311.9999 | 102 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.3 | 153.8 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 16.8467 | 13.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1575 | 700 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.5 | 15 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 927.6666 | 121 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1255.92 | 209.32 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 80.5 | 23 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 464.4 | 344 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1333.8165 | 419 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 168 | 28 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 279.1666 | 67 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16612.7331 | 844 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111.6666 | 67 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.2499 | 111 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78.5833 | 23 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132 | 66 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 627.55 | 163 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8770.3 | 469 | 1 | 1 | 0872-Soot blowers - water | U1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15101.8 | 469 | 1 | 1 | 0872-Soot blowers - water | U1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.3333 | 25 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2152.5332 | 128 | 1 | 1 | 0872-Soot blowers - water | D2-Forced - Delayed | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 879.7499 | 310.5 | 1 | 1 | 0872-Soot blowers - water | D3-Forced - Postponed | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 87.2 | 21.8 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177.205 | 18.3 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 390 | 78 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4966.5 | 301 | 1 | 1 | 0876-Soot blower controls | D3-Forced - Postponed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 607.9999 | 240 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 27 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1074.01 | 32.06 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112 | 28 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 327.6466 | 82.6 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 321.8666 | 136 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 657.9 | 102 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 963.3332 | 340 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8287.5 | 250 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13980 | 300 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.4166 | 67 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 367.5 | 98 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 731 | 172 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1017.5 | 110 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.2666 | 104 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.6666 | 40 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 808.3333 | 50 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 427.9 | 66 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1749.3332 | 128 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.2267 | 22.4 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.8333 | 190 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 897.4333 | 247 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 473.2 | 104 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480.6666 | 70 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 879.8832 | 403 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 11 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.9166 | 95 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267.6666 | 110 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.1833 | 7 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 325.6066 | 44.2 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.3333 | 8 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.2333 | 9.1 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 880 | 110 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1.0667 | 0.64 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4818.75 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201 | 201 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3957.4999 | 150 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5452.5666 | 74 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 6 | 1.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 29.6533 | 6.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 39.895 | 7.9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 138.2333 | 26 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 701.3333 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1225.1498 | 321 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6957.4998 | 345 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7466.6666 | 320 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17336.0664 | 354.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2364.1667 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 947.2 | 37 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.0833 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1845 | 90 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.5333 | 58 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5127.0833 | 115 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 15.975 | 6.75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 29.2867 | 9.55 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 46.2 | 28 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 116.1666 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 134.75 | 21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.8 | 44 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 554.1666 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 644 | 161 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 828.3333 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 15.12 | 5.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 22.1667 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 12 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 21.25 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 87.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 250 | 25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1435.5 | 319 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2479.25 | 47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.4 | 9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.3333 | 44 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.8 | 64 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2189.5 | 151 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 18 | 1.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 8.6955 | 5.27 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1241.1998 | 321 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2246.3999 | 324 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1403 | 122 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4686.3333 | 85 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4689.1666 | 85 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.75 | 21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 9.1583 | 3.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 26.915 | 7.69 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 152 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1439.1499 | 321 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1738.7998 | 324 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 720 | 20 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7696.3166 | 163 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1260.4 | 137 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1705 | 155 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3748.0999 | 222 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2040 | 170 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 19.2092 | 6.23 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 19.2 | 18 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2717 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 33.8333 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 133 | 19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 181.5 | 33 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 187.55 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1257.2498 | 321 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 593.9999 | 162 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 744.1667 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740.8333 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248 | 124 | 1 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 641.1166 | 143 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 12.1333 | 26 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 65 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 113.6 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 36.75 | 21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 73.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 101.75 | 33 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 226.6667 | 17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1166.2999 | 321 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1936.3331 | 314 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.0166 | 49 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3447 | 383 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8776.25 | 425 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1658.65 | 147 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372.75 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660.3 | 186 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1136.25 | 225 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1584 | 132 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1887.5 | 151 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2282 | 163 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 32.5833 | 23 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18.1 | 6 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1263.6 | 324 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1280 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 347.75 | 39 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 151.35 | 9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 7682.0333 | 82 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 8.7 | 9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 100 | 25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 217.6 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 322.5 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 544.9833 | 19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2352.4733 | 211.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 34.15 | 6.83 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 23.6 | 6 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 260.2667 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 552.6783 | 56.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 589.2533 | 116.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 833.4383 | 19.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2822.265 | 106.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 16585.2 | 15.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 63 | 6.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 119 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 134 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 64.575 | 6.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 314.65 | 20.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 15.05 | 4.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 69.1167 | 14.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 326.2 | 23.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Summer | 76.2 | 25.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 99.75 | 13.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 20.5 | 10.25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1344 | 448 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1226.6666 | 230 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2440.7499 | 195 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1657.9999 | 120 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 343.2 | 264 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 417.32 | 104.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.99 | 10.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 732.0833 | 175 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1449.42 | 241.57 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3182.04 | 176.78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 47.8333 | 7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 113.4 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2436.1665 | 470 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3032.0816 | 204.41 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74442.06 | 811.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 52703.7331 | 598 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2085.4166 | 275 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.2572 | 15.17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 417.7897 | 8.71 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 448.14 | 20.37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 552.78 | 30.71 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 556.02 | 92.67 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3381.95 | 307.45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 345 | 69 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 364 | 91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 838.08 | 46.56 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1150.71 | 104.61 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3934.7466 | 74.9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1305.4833 | 37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1239.9999 | 150 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 302 | 75.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 898.02 | 149.67 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3335.91 | 107.61 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1443 | 130 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1869 | 267 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3692.3332 | 212 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234.5666 | 227 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 253 | 126.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 305 | 305 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17491.5 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 109118.3331 | 658 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1495.48 | 53.41 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1343.9999 | 180 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.96 | 6.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2584.9999 | 330 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138 | 27.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 282 | 35.25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 142 | 35.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 190 | 95 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 286 | 143 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 688 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1581.02 | 112.93 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5513.04 | 76.57 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5515.8 | 95.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 460 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2104.3732 | 232.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4815.4331 | 571 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25208.65 | 167 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 842.8333 | 130 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1028.35 | 157 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1381.3332 | 224 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5582.3831 | 413 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6255.3333 | 220 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17072.25 | 255 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.9128 | 6.43 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284.2667 | 41.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117 | 117 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 148.74 | 49.58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 809.97 | 42.63 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 543.06 | 38.79 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1257 | 104.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1467 | 81.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1608 | 134 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 168 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3440.3498 | 249 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19727.7799 | 437.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2454.1665 | 190 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.44 | 37.48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 378.95 | 34.45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 429 | 71.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 623.04 | 51.92 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 451.98 | 75.33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 726 | 121 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 913.92 | 152.32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1116.2 | 279.05 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 234 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1557.75 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57192.96 | 812.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 979.9998 | 600 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10541.3947 | 437.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.9342 | 8.05 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1369.3532 | 312.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555.9998 | 240 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3775.9999 | 240 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79 | 19.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 868 | 124 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3304.3332 | 230 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45 | 22.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 488.16 | 81.36 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.94 | 58.47 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1022.04 | 56.78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 368 | 184 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 631 | 126.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1048 | 104.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6233.14 | 132.62 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 87 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1140.085 | 213.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11655.9997 | 437.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 101.2 | 9.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 31.2 | 5.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1072.9999 | 111 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 31.2633 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 730.1667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 29.1917 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 212.965 | 22.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 4.7917 | 2.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 80.9833 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 103.675 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 584.3333 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 527.5 | 21.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 142.6 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 348.75 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 97.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 65.2 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 339.6 | 28.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 51.5 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 401.005 | 25.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2145.3667 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2290 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39.525 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1410 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 45.5 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 282.725 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 396.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 567.3 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 24.15 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 49.45 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 127.125 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 129.625 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 466.2 | 33.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 418.0133 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 29.6 | 6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 71.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 539.15 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | WECC | Winter | 8.7 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 711.3333 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 141.29 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 644.8667 | 17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1062.1333 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4049.75 | 167 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 21 | 4.2 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 12 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 528.3665 | 262 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 163.75 | 131 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 12 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1844.9999 | 135 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 823.5 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1560.1666 | 230 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 143197.6 | 364 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3795 | 345 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 37.5 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 6.02 | 0.86 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1975 | 100 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14708.2832 | 511 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.8833 | 187 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 378.225 | 12.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17984.3833 | 193 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26418.7 | 658 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 290.5533 | 16.4 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 26.3667 | 11.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 586.5 | 170 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 659.01 | 219.67 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15548 | 598 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62037.7332 | 364 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1205.9998 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 985.5 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3780.6665 | 214 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 345.99 | 115.33 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1494 | 149.4 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5746.5332 | 262 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 749.1666 | 155 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1115.9999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1747.2 | 224 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1007.9999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 337.5 | 15 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 696.4666 | 31 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3019.895 | 47.1 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2619 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216 | 6 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1332.5 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5532.9999 | 165 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 453.6 | 336 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.5 | 245 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 163.954 | 41.16 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 868.4998 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.521 | 42.33 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6588 | 216 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124 | 62 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.24 | 38.62 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 115.6883 | 33.86 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1093.5 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1768.8 | 144 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 319.525 | 255.62 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.215 | 85.62 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1734.04 | 157.64 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2333 | 233.3 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9368.4 | 42.2 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 414 | 207 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.5 | 78 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1257 | 209.5 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.32 | 38.88 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132.288 | 49.92 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 220.0408 | 37.19 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1550.01 | 221.43 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1745.8331 | 419 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32615.4996 | 555 | 1 | 1 | 0895-Ashpit trouble | U1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5746.6666 | 160 | 1 | 1 | 0895-Ashpit trouble | U1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 488 | 305 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 815.75 | 251 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 702 | 36 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1709.9999 | 270 | 2 | 2 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 229.1167 | 23.3 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.41 | 52.41 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4224.6164 | 343 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3510.2332 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 247.42 | 26.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 419.2 | 9.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 856.8 | 204 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 839.6999 | 162 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5427.6665 | 380 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16321.2497 | 825 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7587.833 | 530 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14121.7996 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.64 | 80.64 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1530.1645 | 240.34 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.6925 | 198.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 251.8 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 706.3333 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 131.4033 | 15.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 748.1998 | 261 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65604.4997 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301.28 | 150.64 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 959.91 | 391.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1731.87 | 247.41 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 853.98 | 142.33 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 14.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 152.25 | 14.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1517.1166 | 227 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2657.8 | 274 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3285.7 | 319 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 231.28 | 115.64 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 441.1733 | 240.64 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 880 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 597.2666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1910 | 191 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2627.0832 | 325 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1180.9 | 241 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1084.7998 | 288 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6441 | 339 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26584.9997 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 230.64 | 230.64 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.9333 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1786.4725 | 246.41 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.4664 | 379 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 856.8332 | 265 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 646.5666 | 163 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 957.5332 | 271 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66440 | 800 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 43266.6665 | 590 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12289.2 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14801.033 | 458 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.4 | 116 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.8775 | 131.51 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1397.0665 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4458.5 | 370 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 473.6333 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 16.5 | 11 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2663.6666 | 305 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23848.5 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89849.4999 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 709.9 | 93 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.2925 | 89.17 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.3025 | 201.21 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.47 | 238.47 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 832.4332 | 221 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 838.7833 | 11.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 586.5333 | 166 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2264 | 283 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2599.5999 | 291 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2928.3331 | 350 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.41 | 102.41 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.8333 | 2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 240.5 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 588 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 144.375 | 16.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 731.25 | 25 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 692.7467 | 24.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 507.6332 | 194 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11296 | 353 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11147.4999 | 390 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 800 | 75 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 92.95 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 982.8 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 390 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1701 | 45 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176.6666 | 100 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.8333 | 115 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2372.5 | 365 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D2-Forced - Delayed | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 606.6667 | 25 | 1 | 1 | 0899-Bottom ash controls and instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 727.1999 | 216 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292.5 | 130 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 269.4333 | 118 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 650-Fluidized Bed
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 885.4166 | 125 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39295.9 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39602.5 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3797.4999 | 150 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.5 | 54 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26584.1332 | 364 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U3-Forced - Postponed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12857.53 | 49.8 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 861.4667 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 867.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1118 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 353.3833 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 854.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 858 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1811.3333 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 5073.25 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 14.7333 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 507 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 620.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3323.6667 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 675.35 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 556.9833 | 23 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1230 | 40 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 12.6667 | 8 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 2144.9999 | 198 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 236 | 4 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 4447.8167 | 23 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 3488 | 40 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6161.0999 | 198 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40957.8165 | 193 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4908.3333 | 50 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1000 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 497.375 | 28.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 702.45 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2476.25 | 105 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5966.2499 | 225 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14586.6666 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.9166 | 115 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7890.6665 | 220 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 363 | 72.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 754.05 | 150.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 56.73 | 18.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 40.5117 | 22.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 84.315 | 21.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 27.6033 | 16.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 168.7666 | 24.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 27.6833 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 40 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.5 | 114 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2946.78 | 163.71 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.3708 | 48.89 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 433.9999 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 912.5 | 365 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3603.75 | 465 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4525.9998 | 465 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 231.325 | 28.5 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1146.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16404.2333 | 199 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1547 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1891.2 | 144 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4100 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 309.75 | 177 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.675 | 118.41 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.935 | 58.82 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2878.7789 | 215.37 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 25.84 | 13.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 73.7917 | 16.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 153.3 | 21.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 167.81 | 19.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 69.3333 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 72.8 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 103.92 | 14.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 7.5 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 24 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 44 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 677 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 144 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.8625 | 59.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.333 | 69.09 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.7814 | 113.61 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9815.1665 | 470 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1371.1483 | 21.1 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1354.5 | 129 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1708 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3403.8 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.0833 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 746.6666 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 876.875 | 28.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.6666 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 237.65 | 49 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1320 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1862.9332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1969.5 | 202 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2043 | 227 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7739.6665 | 217 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133.7523 | 53.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1505.8799 | 192.24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 318.389 | 276.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 356.7 | 142.68 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 2.05 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 34.4667 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 40.3333 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 432 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 170 | 34 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 231 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 308 | 22 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.7121 | 77.51 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.6 | 56 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1649 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1220 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.75 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3889.1666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.75 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 373.3332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 602.3333 | 65 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 764.7498 | 345 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1459.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 23.2 | 14.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 29.14 | 18.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 53.2733 | 24.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 183.375 | 22.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 383.8833 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 13.9533 | 5.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 143.2 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1043.1667 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 6 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 247 | 38 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 928.25 | 395 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43162.4663 | 511 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1161.0666 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1495.4333 | 238 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 244.9998 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248 | 124 | 1 | 3 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 478.3331 | 350 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 630 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 670.9999 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 749.9999 | 360 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 756 | 112 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1005 | 335 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.275 | 45.02 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 308.4 | 102.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 793.4574 | 221.43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 15.0267 | 6.44 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 15.2733 | 7.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 23.6033 | 19.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 33.35 | 14.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 40.4 | 20.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 52.3983 | 21.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 26.95 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 32.8 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 33.1833 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 164.0833 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 104.2667 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 36 | 3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 240 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 36 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 228 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 336 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 518 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2066.25 | 435 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.5903 | 61.61 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.825 | 59.86 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.215 | 113.62 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.9399 | 157.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.32 | 100.32 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6026 | 460 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33 | 110 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 636.5165 | 181 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.6 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.4167 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276 | 138 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1296 | 324 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8176 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.4 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2124.9999 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204.96 | 102.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 11.85 | 7.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 141.1133 | 24.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 130.05 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 180.6 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 60.8 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 285 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 93.5 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 95 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 42 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.7413 | 57.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 326.9092 | 175.13 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 862.5 | 28.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1618.2 | 93 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2603 | 137 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 250.0666 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 291.4 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 294.5833 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 669.1666 | 275 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 705 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1319.4999 | 210 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204.9255 | 132.21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 77 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 62.08 | 19.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 105.2333 | 20.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 136.95 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 952 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.6666 | 131 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.7325 | 62.93 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.9733 | 83.92 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.374 | 75.96 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.133 | 100.14 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4396.8332 | 370 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1069.5 | 465 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 183.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384.1332 | 134 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.2667 | 44 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 519.6 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1375.8333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3295.8333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8483.45 | 383 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1683.7332 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 367.5782 | 191.78 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 108.77 | 21.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 112.2333 | 18.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 42.34 | 21.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 544.7267 | 20.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 122.9 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1117.4 | 6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 94.25 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 336 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 20 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 195.5 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 408 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.1441 | 109.73 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.208 | 55.52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.84 | 77.68 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.88 | 99.88 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119.7816 | 102.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.1 | 61.65 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5421.9332 | 334 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 385 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 97.5 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 505.2667 | 22 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 968.5 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 49.8333 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1049 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 542.9333 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 559.4667 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 220.5667 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1577.92 | 98.62 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 171.43 | 47.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 430.4433 | 26.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 11136.0449 | 123.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 12332.775 | 97.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 557.405 | 39.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2298.66 | 126.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2796.69 | 131.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 5761.4266 | 77.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 3589.6333 | 95.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 45513.0432 | 387.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 232.4916 | 121.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2170.0466 | 127.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 2784.145 | 63.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 584.65 | 106.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 1272.9066 | 82.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 10290.4399 | 245.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 469.4916 | 106.3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 3299.35 | 87.4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 1692.6466 | 87.4 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 391.6 | 88 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 231.25 | 75 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 327.9133 | 97.4 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 300.96 | 25.08 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1287 | 24.75 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0935 | Bed material disposal conditioner | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1287.99 | 117.09 | 1 | 1 | 0935-Bed material disposal conditioner | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2383.3333 | 100 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3395.8333 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 11502.075 | 326.3 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1253.1665 | 365 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 101.25 | 405 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 15869.7499 | 285 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 250 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 4401 | 163 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 729.1666 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 5128.8965 | 325.3 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 7043.7496 | 525 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 7603.7498 | 525 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 14326.6665 | 280 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 39 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 81.25 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 320.6667 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 23.4 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45.5 | 26 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 260 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 96.4167 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 28.1667 | 13 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0973 | Flue gas-solids separator refractory | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 108.9333 | 43 | 1 | 1 | 0973-Flue gas-solids separator refractory | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 2718.0907 | 37.76 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 24.7 | 38 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 66.6666 | 40 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 135 | 50 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 606.25 | 5 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 26880 | 80 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 43.3333 | 40 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 63 | 10.5 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1392.4166 | 245 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2872.0665 | 268 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 4757 | 268 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 239 | 20 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 201 | 13.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 444.6 | 24.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 5304 | 221 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1451.6666 | 50 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 909.448 | 37.92 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 72.6666 | 40 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 86.25 | 15 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 4.2667 | 8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 70 | 30 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 112.8 | 14.1 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 10.56 | 35.2 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 18.9 | 18 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 4667.6665 | 268 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 48.3333 | 10 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 907.0497 | 37.82 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 4357.7947 | 36.32 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 23.4333 | 38 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 129.5667 | 23 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 144.3 | 78 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 48.3333 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 945 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3762.0833 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 34335 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6010.5 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3153.2466 | 157.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | WECC | Summer | 4192.9999 | 84 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 851-CC GT units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 333 | 74 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 851-CC GT units
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2016 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 2062.314 | 56.97 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 860-Co-generator Block
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 5739.6666 | 26.8 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 862-CoG steam units
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1283.3332 | 140 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 254 | 127 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7992 | 72 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.1 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 764.5 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2494.0667 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.6666 | 130 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.9332 | 128 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3056.2616 | 53.65 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 900 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 270 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 633.96 | 11.74 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2750.29 | 240.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 228 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 657 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 291 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 235 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34969.0448 | 746.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16803.1329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 763.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9869.3166 | 66.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10823.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11284 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17361.25 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23337.1165 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40366.3332 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43335.5 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45781.3331 | 640 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50816.4 | 564 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71971.4332 | 334 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 991.35 | 9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3131.0332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3534.6999 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6584.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7864.13 | 47.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8309.5833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11825.2582 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12619.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12812.3333 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12941.25 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20237 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21690.9497 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30001.2 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31254.8664 | 379 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38315.2 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54254.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61252.0998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 70327.169 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6038.2 | 266 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7358.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10904.7 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12391.8666 | 241.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15571.4 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16575.1032 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18737.1665 | 242.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22983.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29629.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3790.2999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11300.4666 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31254.5 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20115 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28344.5 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 45958.05 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8450.1999 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48404.9998 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5265.8666 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51375.45 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31248 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 120138.75 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1368 | 76 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12644.8131 | 575.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45602.2161 | 817 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2278.5 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5606.504 | 264.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2079.15 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.8667 | 8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.3998 | 267 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24815.2666 | 137 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 251.6 | 6.29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 650.1333 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 679.2 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1000.14 | 12.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 710.6867 | 15.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1915.8333 | 55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2616.0866 | 42.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 413.8 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1700 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2052.4666 | 68 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2854.9999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7992.5999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11336.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17993.55 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18093.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 24590.6132 | 241.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25631.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27627.6 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 29616.4 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45000 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52549.3329 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97834.6662 | 640 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103939.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154409.9681 | 814.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1487.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3278.5 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4451.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4631 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5888.75 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5976 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9450 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11334.833 | 470 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 13984.2265 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15852.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 18324.215 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20862 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25937.1 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29091.75 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29200.5 | 515 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35067.5 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35428.0831 | 311 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41450.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46860.4998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67497.3329 | 713 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106610.3663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6275.1333 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11489.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19920 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24642.3332 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137005.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26208 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 28792.4165 | 365 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 34482.5 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2276.3999 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3355.9999 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9115.9999 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10074 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 26314.5999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 49167.25 | 522.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 75087.3332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 167367.1995 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 3812.1666 | 102.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 26719.225 | 432.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 29142.345 | 432.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 29957.2632 | 432.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10411.0997 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30927.7497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49961.7 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64804.8 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7525.5 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8650.6999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24015.7498 | 639 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26530.7163 | 517 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30033.9 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14761.8 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183991.9497 | 783 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58074.1665 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5162.945 | 47.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 645 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9988.55 | 127 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 754.7833 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54238.9994 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25789.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15907.9996 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 6043.9497 | 445.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1835.4 | 63 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2033.1163 | 613 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7457.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10905.4165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11766.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24114.9995 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29500 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39005.2 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46329.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50523.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68627.1664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74173.35 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80724.9998 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7362.8 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8530.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8730.0999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 13057.1382 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21029.5166 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21471.1833 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21984.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27936.4163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33415.55 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41942.9995 | 811.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46924.6581 | 814.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54835.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4491.6666 | 55 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9600 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14104.333 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20501.9997 | 459 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22000 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24542.6665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46005.3331 | 760 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70776.75 | 1265 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87675.15 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112045.9996 | 1320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 35137.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48061.9994 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 28222.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 5392.8 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 23737.2266 | 340.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3305.9997 | 495.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10491.76 | 335.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 13397.4995 | 699 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16292.05 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11276.2499 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12366.9332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16219.5832 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16255.9831 | 371 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17829.9 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29532 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14265.5 | 554 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20868.3999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32413.3332 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35821.5 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47760.6665 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77554.5165 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145389.6 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14400 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31395.75 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36545.0163 | 511 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124541.5 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32704.62 | 358.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2498.4998 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29562.8664 | 364 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53860.0832 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8913.8999 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.5 | 49 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 859.6667 | 5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2149.2833 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 242 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 345 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 471.3 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 357.115 | 12.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 363 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 919.5833 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1134 | 13.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 340 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3237.9 | 753 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1037.9833 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 6266.9366 | 42.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 167 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 315 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 753 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 11305.2997 | 786 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2580.15 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5455.3332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6964.2666 | 64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6972.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7969.4333 | 106 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8546.1665 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9056.1013 | 141.76 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10486.1666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13381.6665 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14711.0333 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18427.7332 | 448 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43271.7997 | 858 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49873.2 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70990.2197 | 812.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122950.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1131.6665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2758.85 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3740.8331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7442.5831 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 7675.56 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9350.8333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10674 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10810 | 470 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11259.325 | 584.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12410.6666 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12607.5666 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13221 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14542.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16452.5998 | 306 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18875 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19642.1666 | 134 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 21419.42 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27251 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27550 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30406.4163 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31182.9331 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35766.8331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39800.5665 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60424 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80386.35 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151754.1664 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214528.6 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4199.85 | 459 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15163.9998 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27724.85 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28751.45 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30549.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54558.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88948 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34285.3331 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2236.8 | 64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 8123.3999 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4352.0132 | 335.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6408 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16884 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 54895.8331 | 775 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 100724.7999 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 10238.88 | 102.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 20648.19 | 447.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12581.2499 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9193.8 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14543.6666 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18968.8999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25757.7999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29720.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53655 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27906.3 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40866 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2595.55 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15847.65 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70749.4664 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74799.118 | 536.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31611.0663 | 616 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.1667 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3342.4665 | 277 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.5 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.6666 | 145 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1266.3 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20606.1331 | 332 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1164 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 856.5025 | 17.85 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 672 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 45.4166 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1663.8766 | 42.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 492 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 498 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9956.6665 | 515 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3443.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4429.75 | 611 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8235.2833 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10308.8831 | 607 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16070.8665 | 446 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18716.9998 | 612 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 20085.1716 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22740.3 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28249.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31105.2 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38540.616 | 746.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39763 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44548.3997 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66499.25 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106501.9996 | 1320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199.1667 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2448.5 | 49.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5003.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8284.9999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9171.1999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 10758.2933 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15954.7499 | 189 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 16728.14 | 584.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22745.6665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23836.8332 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27783.5 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39183.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40388.5331 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49210.5663 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53097.5 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65953.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92233.45 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113737.9997 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3379.95 | 63 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21323.1 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85549.8663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104504.3163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162637.2 | 594 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35335.9994 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 37022.84 | 335.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 167431.2666 | 109 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 43650.7999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 19413.3 | 397 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 183331.5 | 333.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 58828.275 | 445.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7992 | 222 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18167.3615 | 265.54 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4312.9999 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27288 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9985.5 | 570.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11700 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24694.0831 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37117.3329 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43554 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55554.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1918.91 | 47.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85813.3328 | 800 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34986.6661 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5890.5 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 247.7166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1265.4791 | 28.75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3186.48 | 312.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 953.3999 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5133.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1170 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1617 | 77 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3588.75 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16626.4999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 807.5 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 657 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 870.33 | 12.99 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28566.733 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11412.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14416.25 | 607 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14622.3 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20800 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 21668.4532 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23659.4665 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28389.1 | 626 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33673.6 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43690.8329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50786.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64728 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80779.6662 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103725.3663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3647.1666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5129 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6867.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7338.3333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7435.14 | 49.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8270.1 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 10834.5215 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 24248.9133 | 233.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 27255.345 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31407.5333 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 43905.8329 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44217.1665 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6914.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8279.1333 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12152.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17599.6 | 184 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 25905 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32288.9994 | 846 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40913.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51985 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 46721.2496 | 675 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5880.3331 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 518.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3698.1 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2832.9 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9945 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17498.4 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37525.5999 | 168 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 75308.333 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 99381.2664 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 191298.6499 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 13800 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 38313.6 | 62.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 247997.52 | 333.33 | 1 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 7650.4997 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10164.4999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23218.65 | 441 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34251.5 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80212.4991 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6690.8333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18620.6666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28547.0163 | 517 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32482.1999 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56073.3332 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17640.7499 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24748.8328 | 815 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6058.3332 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1255.5 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5266 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 366.3333 | 157 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.6666 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20189.6331 | 329 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 560 | 14 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 876 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1807 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 451.4 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1135.4166 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 2149.42 | 23.62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 375.2 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16.6666 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 66.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 102.4666 | 58 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1100 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 375 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5776.2999 | 141 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2871.1667 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10686.6331 | 613 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32731.9994 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.5 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6854.25 | 195 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11498.4259 | 390.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14397.4166 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16633.5998 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18660.4832 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27752.1831 | 299 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54888.75 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74716.1662 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78915.45 | 723 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92989.1658 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147857.4162 | 1265 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2633.3332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6439.9999 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6955.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7155.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11073.03 | 49.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14369.8331 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15239.5833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 16993.6266 | 236.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18742.35 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23092.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30000 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33548.1998 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38545 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58094.4 | 336 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60668.5 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60940.8163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78725.5 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151279.3328 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8781.3328 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14234.0998 | 306 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17290 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20865.7665 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26076.1995 | 723 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30496.0663 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34063.7464 | 354.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45319.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46114.7498 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49535.45 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74500.3163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103638.8163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1966.3416 | 104.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7161 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 13212.4664 | 335.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20914.4 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37774 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 39928.2499 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 317007 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 11010.9999 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 12219.9999 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10593.3333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5189.3333 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8981.8664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16831.35 | 331 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56881.9994 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 87910.5999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10294.2 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70217.0663 | 496 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19886.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4572.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12091 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.2166 | 77 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1330.9998 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5168.9 | 127 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14033.1499 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 87.6033 | 8.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 889.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1214.5832 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2331.45 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2673.3 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 362.25 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 248.325 | 12.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 435.6 | 13.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 656.25 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1369.0667 | 30.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 139.4866 | 42.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1197 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 691 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14787.4996 | 525 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 36058.0823 | 505.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5160 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5815.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9770.9 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10318 | 469 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10597.1666 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13458.7405 | 175.13 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19620 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19886.3108 | 746.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20966.7998 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24378.6666 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28965.4 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31248.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32442.6665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38426.2 | 839 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56960 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118438.8663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3431.5633 | 21.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4991.5 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5122.2666 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6012.8999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6191.9665 | 446 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6772.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6787.1665 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16387.25 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18231.2665 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18991.2 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19204.7333 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25661 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37950 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40345.7 | 626 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56622.6 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70771.3328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93375 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104848.3328 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114357.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183409.0663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17130.8999 | 153 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19670.0766 | 241.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20106.3497 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29254.3998 | 336 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71280 | 594 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92757.8162 | 637 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26613.9997 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32103 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 41940 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4139.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 56087.6164 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 61904.8499 | 171 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 171763.8 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10436.9066 | 92.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 10140.33 | 106.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 32200.0914 | 432.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 34491.4514 | 406.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 68807.5831 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 103993.4044 | 333.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22142.7 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71540 | 700 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12417.7999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14363.98 | 49.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17170.9999 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44366.4 | 711 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21030.4 | 496 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 35882.49 | 337.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 325 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 21060.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 21480.2 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 19792.5333 | 136 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 22785 | 155 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 8370.0331 | 293 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 46.5 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2728 | 35.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1399.5 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2846.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 874.13 | 18.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1153.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OL | 800 | Miscellaneous | NPCC | Off-Peak | 527 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2186.0227 | 24.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1092.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1290 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 20468 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 43.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 596.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 805.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 986.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 439.52 | 16.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 896 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 851 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 668.255 | 18.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 544.8667 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1540 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 22495.9998 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1417.3333 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1906 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 600.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 6069 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 670.2133 | 16.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2130 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 564.16 | 16.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 920 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1063 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | WECC | Summer | 343.8967 | 24.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 249.5417 | 11.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 331.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 445 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1012 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2005.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 922.7666 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 36930.2999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 12645.5999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 20097 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 60.8 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 697.5 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 693 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 3417.1667 | 35 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1985.0667 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 32.3 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1244.75 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 467.1333 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6526.7665 | 29.01 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 597.3333 | 14 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1113.9333 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 346.5 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1018.25 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2738.45 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 13757.5499 | 369 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 506.0333 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1354.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1365.3333 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2240.15 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 930.5 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1132 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 22495.9998 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 850-Combined Cycle Block
1000 | Waterwall (Furnace wall) | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 20468 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 850-Combined Cycle Block
1000 | Waterwall (Furnace wall) | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 6069 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 850-Combined Cycle Block
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37460.08 | 354.4 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14394.0666 | 142 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 23586.5497 | 831 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28945.5 | 839 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7056.66 | 49.8 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 2456.2333 | 31 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24049.3332 | 272 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27594.65 | 589 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24146.85 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 170 | 170 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11349.05 | 61 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5554.4 | 106 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18313.2666 | 142 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52170.9996 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14846.3233 | 60.2 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 630 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 800-Miscellaneous
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1120 | 32 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 800-Miscellaneous
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1000 | 40 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 800-Miscellaneous
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 101.1998 | 276 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | SF-Startup Failure | 800-Miscellaneous
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1518 | 33 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20829 | 318 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2110.5833 | 31 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2295.85 | 37 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5485.5 | 106 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 8627.9999 | 144 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17272.6998 | 318 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1648.1333 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3836.7667 | 47 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28599.4995 | 705 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1425.6 | 33 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58410 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 412.2 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40902 | 510 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 459 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 511.5 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 695.5 | 13 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1602.7166 | 37 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4964.9999 | 90 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3444.5 | 830 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1529.9999 | 108 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13148.75 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | SF-Startup Failure | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43011 | 590 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12024 | 334 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9911.8366 | 137.03 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270 | 135 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 361.25 | 28.9 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 644.831 | 105.71 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12917.6 | 48 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 366.6666 | 100 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5520 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17500.005 | 47.1 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28677.8 | 446 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 267.1667 | 35 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25956.9166 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27620.75 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23361.6 | 47.1 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19862.9166 | 95 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3645 | 90 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5265.75 | 35 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24107.8333 | 38 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5802.7093 | 141.76 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46118.3331 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 34818.24 | 362.69 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.85 | 11 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4184.7499 | 285 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15981.9 | 174 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27109.5999 | 168 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15591.65 | 199 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15284.88 | 358.8 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13948.9999 | 195 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20600 | 515 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270295.6664 | 770 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1541.8333 | 58 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5373.8666 | 176 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16313 | 220 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8403.3211 | 175.13 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16562.5 | 250 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23833.3329 | 650 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19521.9 | 199 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23710.5 | 330 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7687.5 | 250 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42924 | 280 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16932.0664 | 364 | 1 | 1 | 1020-Convection pass wall (water tubes only) | SF-Startup Failure | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23474.4665 | 446 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 2928.2 | 66 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Summer | 4768.5 | 66 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Summer | 4381.3 | 66 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 15726.7 | 66 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Summer | 3390.2 | 66 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 800-Miscellaneous
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 12765 | 345 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18376.9998 | 690 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29355.1998 | 336 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.7333 | 62 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1258.5 | 18 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20995.3333 | 220 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6383.1841 | 128.65 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19175 | 325 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55878.9997 | 510 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206946.4 | 334 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38610.4995 | 705 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4414.7998 | 234 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5352 | 446 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37739.033 | 446 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17356.833 | 446 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11541.4 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.7 | 69 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69172.6665 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 106406.4 | 136 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 250 | 250 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16058 | 280 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24976.1959 | 390.66 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87215.3332 | 280 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47520 | 600 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134.7499 | 165 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 85 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36089.9498 | 507 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25045.1665 | 190 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127609.9998 | 600 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88339.9998 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122970.2795 | 812.4 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7233.2 | 107 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56610.9 | 723 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168937.2897 | 815.4 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100081.4097 | 811.8 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107752.6663 | 520 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 169720.3195 | 811.8 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47906.6 | 266 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75177.7998 | 354 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 170 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 401.9165 | 371 | 1 | 1 | 1035-Platen superheater | D3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64903.41 | 811.8 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 55152.5 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 12136.9332 | 454 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51654.4998 | 510 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85 | 85 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 336 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2307.6666 | 70 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8119.3333 | 190 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46199.7 | 639 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155412.4995 | 750 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11583.6665 | 620 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 50222.0331 | 598 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 19526.3999 | 162 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 27957.9999 | 210 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29941.75 | 523 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37597.8 | 446 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 705.7332 | 158 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 29195.28 | 377.2 | 1 | 1 | 1035-Platen superheater | SF-Startup Failure | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41856.0997 | 858 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20969.3695 | 815.4 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 49853.2663 | 598 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83390 | 620 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22942.4665 | 262 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 315 | 60 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20796.75 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23976 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175804.1996 | 594 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31376.1 | 446 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76859.1662 | 745 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5952.9066 | 35.2 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3816.8533 | 35.2 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2778.75 | 285 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 19940.6665 | 280 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1136.6665 | 310 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 10502.25 | 285 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 539.5 | 13 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 150.01 | 85.72 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 214.6666 | 80 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6402.9998 | 570 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10145.6666 | 110 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 786 | 24 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 843.75 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.6025 | 178.41 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3262.2998 | 606 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20874.6665 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25654.9665 | 307 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30024.6663 | 580 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 84251.4663 | 592 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 60939.36 | 335.2 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3022.942 | 60.58 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37360.3331 | 347 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35234.0829 | 593 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25090.0832 | 505 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33470.2831 | 353 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.1775 | 88.71 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20984.1662 | 745 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40913.7665 | 482 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27694.4163 | 565 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46906.633 | 482 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71883.3332 | 475 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114627.3328 | 770 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17576.3 | 238 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18814.6199 | 104.4 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34041.25 | 565 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58029 | 580 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4158.1 | 86 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 9541.25 | 425 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 106665.6 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110585.6665 | 590 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19514.5998 | 318 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25531.9997 | 390 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9116 | 132.5 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 254.9166 | 95 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1646.6663 | 520 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24746.6663 | 580 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28676.2665 | 611 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38142.7331 | 362 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76346 | 590 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78035.7497 | 507 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1840 | 200 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11161.6665 | 362 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16800 | 200 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89934.25 | 595 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 34141.9999 | 258 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 110054.4548 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1100.5366 | 60.58 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20350.4665 | 458 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23688.7 | 602 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.1333 | 16 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.41 | 115.47 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 924 | 24 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39362.5 | 670 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90138.25 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20278.3 | 491 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31236.7998 | 336 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10368.8665 | 476 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10906.1733 | 101.8 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82820.8329 | 650 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109930.1328 | 872 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Winter | 38640.36 | 642.4 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.88 | 55.47 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 344 | 40 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2524.5 | 297 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2020 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.5775 | 242.31 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8975 | 100 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13767 | 260 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40263.6665 | 395 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12820.1665 | 485 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20134.8 | 564 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21115.3331 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 37826.6666 | 80 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 9686.601 | 50.22 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 3567.1523 | 60.58 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7136.3998 | 342 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19155.7 | 446 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13590 | 151 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30222.6831 | 353 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 571.41 | 190.47 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 630.0395 | 245.47 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1135.4165 | 545 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1635.3666 | 142 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240 | 10 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1515.28 | 32.24 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13397.5332 | 266 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 13747.8463 | 598.6 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13740.2499 | 255 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15390.6665 | 485 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20377.5 | 275 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29798.1 | 339 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4008.3329 | 650 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10476.6665 | 175 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17642.2665 | 307 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35081.2 | 616 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32172.085 | 496.1 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10144.583 | 485 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32901.9165 | 605 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.1666 | 70 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.7333 | 196 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 114.7499 | 81 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 902.82 | 150.47 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 704.4 | 18 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38373.6665 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45542.9 | 661 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133210 | 770 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16580.1999 | 273 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24436.25 | 565 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31027.9163 | 565 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112327.5 | 850 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40264.5 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11812.0999 | 258 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 32192.333 | 437 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 27235.0829 | 605 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11836.8331 | 290 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21179.49 | 101.8 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 29452.8331 | 610 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68831.5 | 505 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2744 | 42 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 435.3 | 18 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.6025 | 314.41 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.855 | 221.71 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13650.5832 | 245 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3508.5 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20530.0665 | 259 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53360.9998 | 594 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49329.9996 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 44850.7665 | 437 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9564 | 80 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27860.133 | 446 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6341.25 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36661.8 | 588 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8820.97 | 101.8 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10021.5499 | 231 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18658.2082 | 132.5 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 48958.8266 | 331.4 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1056 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1852.6666 | 40 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 299 | 13 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 92.6833 | 8.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 223.2 | 9.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 168.3 | 15.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 229.245 | 15.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 276.9 | 21.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 288.15 | 11.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 243.8917 | 11.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 933.3333 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 11543 | 238 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 226.4283 | 10.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 271.2 | 11.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 454.6667 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 466 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1214.9616 | 31.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 9957.4999 | 150 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 365.3333 | 80 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 30455.6999 | 198 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 15497.4999 | 150 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 11543 | 238 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 850-Combined Cycle Block
1040 | First superheater | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 2250.9666 | 77 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 851-CC GT units
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170.9998 | 513 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444 | 148 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 839.7632 | 263.8 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315.5 | 30 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 340.1291 | 112.75 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 443.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 586.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 699.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29354.6666 | 320 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75415.9996 | 1320 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2948.7406 | 129.71 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18609.4999 | 195 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19091 | 340 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22777.2165 | 193 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107977.4995 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186464.3663 | 971 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51614.82 | 815.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86455.25 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22600.6663 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 14.25 | 28.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 173365.9598 | 509.7 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60457.8332 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68023.5 | 606 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46044.0497 | 507 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28790.55 | 411 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33587.0831 | 745 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.2 | 120.8 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 48 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 560 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 581.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6674.4332 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55417 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13543.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30856 | 665 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51577.1664 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74086.2199 | 358.8 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105965.3331 | 395 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22437 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38025.45 | 687 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8223.7499 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21437.6999 | 342 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.45 | 257.8 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.28 | 366.4 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.575 | 294.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.4664 | 686 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 485.8331 | 550 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 658 | 188 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 877.3332 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 439.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 685 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1125.85 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 443.9 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7759.9332 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10230 | 330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20718.5498 | 339 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39802.0831 | 625 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82114.8533 | 216.7 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18810 | 100 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24151.1665 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 69843.0164 | 659 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100101.4996 | 615 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159736.86 | 815.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9829.1665 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26725.4164 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17969 | 151 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.25 | 409 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 249 | 83 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 664.2981 | 238.67 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1819.3301 | 51.71 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1132.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1041.9 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26125.2 | 472 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15272 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24524.1333 | 184 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25729.1665 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45976.6664 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53150.8995 | 687 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66363.9998 | 705 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4223.8666 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13038.6664 | 770 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66673.9993 | 1110 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72697.5829 | 1315 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4578.6 | 78 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56376 | 783 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 582.6666 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16167.4 | 458 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33775.533 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34565.6665 | 605 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53917.5 | 395 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9155.2499 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11031.7499 | 135 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11985.2396 | 204.41 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.025 | 208.1 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125 | 30 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 606.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 973 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 474.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3849.3333 | 80 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1901.2664 | 361 | 1 | 1 | 1050-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6720 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14536.95 | 199 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36798.1166 | 257 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 137651.5 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19955.25 | 315 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 43811.8331 | 658 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 844.56 | 23.46 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1624.9995 | 750 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 170.7333 | 26 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1360 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 354 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 695.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2004 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9380 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11887.5 | 250 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119464.5996 | 564 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10685.6332 | 218 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14031.5 | 190 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25300 | 184 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36940.9998 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9483.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23801.9165 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65970 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2705.5866 | 52.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110046.6664 | 400 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12499.6665 | 220 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17177.85 | 531 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6527.7332 | 182 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169676.1 | 638 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98713.9996 | 1320 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 629.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 779 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 1072.4 | 11.2 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 881 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 311.6 | 164 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5753.0833 | 85 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35042.3331 | 380 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79408.3329 | 1300 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138824.9996 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9503.7 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20984.1 | 339 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2909.8666 | 64 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12515.5166 | 157 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9463.3333 | 136 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52154.7495 | 687 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16921.3332 | 370 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35718.3331 | 739 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 457.3332 | 140 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 469.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1937.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 41 | 10 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 527.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 1107.9 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1586 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 452.7665 | 289 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1684.6665 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48862.5 | 750 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3902.6 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38119.9998 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9203.1332 | 164 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29401.5 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33738.0165 | 497 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14652.5333 | 184 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24185.5832 | 245 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31082.3332 | 385 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80392 | 416 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4019.8 | 199 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11567.4333 | 226 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 22489.88 | 362.74 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 31327.84 | 340.52 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 67089.3331 | 335 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 926 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1626.2583 | 24.86 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 450 | 25 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 803.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 368.75 | 25 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 224.6833 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1599 | 26 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 474.5833 | 25 | 1 | 2 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 93.225 | 24.86 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 734.5 | 26 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 200 | 25 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 705 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 72 | 288 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1515.9 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 32449.75 | 293 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 2214.6 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 2721.8 | 31 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 695 | 278 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 4306.1667 | 35 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 39049.0833 | 55 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 304743.6 | 108 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 94891.1333 | 83 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57649.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11107.2 | 192 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13291.2665 | 193 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44919 | 644 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166795.9993 | 1110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20591.3331 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24767.0332 | 499 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27838.5 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84937.5996 | 627 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18535.9994 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 63728.9164 | 785 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18867.1998 | 264 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77370.8163 | 613 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61089.4665 | 259 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 41757.3 | 83 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14799.1665 | 602 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23102.096 | 497.89 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129520.1996 | 1251 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85849.3998 | 546 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12669.533 | 476 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 40562.815 | 584.9 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 11752.7499 | 159 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6140.7499 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55853.1998 | 552 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77507.2665 | 614 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204613.1 | 773 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16406.1332 | 517 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41828.5 | 595 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51130.3331 | 595 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72109.7498 | 705 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2062.6665 | 208 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 21100 | 60 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7080.9833 | 59 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52531.3665 | 446 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57173.1664 | 830 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26726.6663 | 475 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56160.8332 | 475 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6859.9994 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3052.8333 | 65 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79422 | 620 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28428.2665 | 353 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 352.425 | 38.1 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2348.0332 | 203 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7465.5 | 315 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4810 | 370 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 103500 | 500 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32903.919 | 497.79 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69649.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125041.5 | 1110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10853.0833 | 235 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11923.45 | 163 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13841.19 | 496.1 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33839.4 | 588 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34086.2496 | 555 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20472.8499 | 213 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 255774.6 | 108 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29163.3329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34780.35 | 216.7 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45994.6665 | 440 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9695 | 175 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12818.2999 | 258 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23587.5 | 370 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7154.5833 | 175 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52105.7349 | 736.13 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126273.3329 | 620 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36272.0149 | 437.1 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15479.1665 | 250 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 40346.1328 | 749 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26364.5899 | 262.77 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 41631.9164 | 749 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.05 | 99 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 497.0233 | 16.66 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 23972.35 | 60.6 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14747.3333 | 220 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21306.9666 | 179 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49106.6665 | 635 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12705.6665 | 470 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12984.9999 | 159 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22718.4499 | 159 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23287 | 580 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44006.2499 | 225 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78075.3328 | 830 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27147.8665 | 476 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27886.7331 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 32990.1329 | 641 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6329.65 | 71 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 23383.3999 | 258 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88006.0998 | 546 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3332.3333 | 65 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 49204.783 | 533 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14396.4 | 258 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22271.6665 | 575 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64217.1665 | 626 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17465.25 | 165 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44111.1999 | 336 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24117.1 | 262 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36184.5 | 255 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52992 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77326.9 | 602 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 17179.5 | 390 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53692.0742 | 662.32 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Off-Peak | 8207.0499 | 159 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 187.5333 | 58 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 386.4 | 23 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11501.5166 | 197 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12671.3005 | 497.89 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21822.3998 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8694.3999 | 192 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16018.6666 | 160 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21722.133 | 482 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32101.4832 | 331 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66235.4 | 644 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18573.3333 | 199 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21786.7665 | 307 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56067.8331 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6578 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4717.9994 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11448 | 106 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 52775.883 | 533 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 614263.5999 | 213 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2474.3333 | 65 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16027.5499 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121323.0995 | 762 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19708.4998 | 315 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72852.5 | 575 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17606.0498 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | TRE | Winter | 17121.7166 | 127 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 800-Miscellaneous
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | TRE | Winter | 33030.0832 | 245 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 800-Miscellaneous
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 63960.35 | 419 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 51180.85 | 419 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 50245.4998 | 369 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36290.5665 | 602 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72849.9996 | 600 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24214.9 | 523 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57519.4996 | 606 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 657.6 | 68.5 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.6 | 6 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280.7998 | 324 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15450 | 515 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50824.0831 | 577 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67163.1661 | 790 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3570 | 340 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18717 | 510 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33860.5332 | 328 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9849.3999 | 132 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51813.3328 | 800 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3838.2166 | 167 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39657.8 | 364 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47259 | 708 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6217.65 | 337 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3478.75 | 575 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131513 | 758 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30804.8 | 208 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56580 | 552 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26598.3665 | 602 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.6 | 476 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78933.3331 | 320 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48150 | 600 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11534.9999 | 225 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 29938.3832 | 349 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22123.7332 | 448 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3564.9 | 153 | 1 | 1 | 1075-External reheater link tubing | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 589.3333 | 10 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 13.1633 | 2.2 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 447 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 662.17 | 13.8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1890 | 54 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1853.2833 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.86996 | 52.2 | 1 | 1 | 1080-Economizer | SF-Startup Failure | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 60 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4191 | 110 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19283.0999 | 342 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41020.5 | 690 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55538.6664 | 472 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3595.2998 | 471 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10261.4166 | 245 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26253.5 | 577 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28086.0663 | 598 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1227.5 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 2166.65 | 51 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31594.8328 | 815 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 298.8883 | 18.7 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 3242.6 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 297.5 | 14 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8350.3333 | 235 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23683.4498 | 471 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53868.7498 | 585 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2651.9999 | 153 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 90487.8329 | 605 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5760 | 45 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 410.4165 | 15.21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1025 | 50 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1048 | 32 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10694.25 | 245 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17010.4999 | 195 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37611.933 | 476 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2794.6666 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6930.9332 | 158 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11956.1498 | 249 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43143 | 876 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158434.5 | 790 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9983.8166 | 167 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34295.4 | 783 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40813.3328 | 800 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9707.4994 | 825 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47544 | 840 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2601 | 102 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3144 | 419.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21263.5 | 215 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 525 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 532.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 705 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28052.5332 | 472 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 45750 | 500 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 905.4 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36465.0831 | 395 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Winter | 13377.1999 | 159 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 326.4333 | 14 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 746.2499 | 225 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32763.4999 | 330 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47821 | 580 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87613.1664 | 385 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1346.7999 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12967.5 | 475 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19602 | 220 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80550 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 728 | 104 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 4013.425 | 60.58 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1770.8333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6935.95 | 133 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14179.7332 | 352 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1266 | 120 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 19.745 | 3.3 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 893.6833 | 29 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4284 | 63 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36001.7664 | 662 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 154857.3328 | 740 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5087.5 | 110 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59070 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2658.8333 | 86 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5584.53 | 52.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1229.1666 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57099.4664 | 364 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12210 | 825 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2843.5 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2059.2 | 99 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2232.3 | 42 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 331.5 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 3700.8833 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2113.1666 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6944.5 | 170 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40374.9998 | 570 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46727.3831 | 577 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14242.5458 | 79.25 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16732.8848 | 495.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31748.2664 | 448 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9664.75 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18768 | 340 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20495.1996 | 528 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 138333.3332 | 400 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19642.3333 | 220 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5301 | 190 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23963.3331 | 700 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4124.2 | 68 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 945 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1311 | 95 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 922.5 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 736.5 | 9.82 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50910 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2078.05 | 69 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24802.0932 | 354.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38278.4998 | 585 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76140.1664 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168758.3328 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3938.4166 | 167 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36112.6331 | 661 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42930 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 752.55 | 52.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6227.8333 | 86 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10272.5166 | 71 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2141.7666 | 67 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36763.195 | 655.9 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 12863.9 | 238 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 4745 | 32.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 6200.85 | 67 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 22948.1332 | 218 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1170 | 32.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 21927.8665 | 214 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 9.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 97.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 278.4167 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 433.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 154.7 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 240.5 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 955.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 22.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 663 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 59.5833 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 110.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 578.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1287 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 289.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1354.95 | 27 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 364 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 229.6667 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 455 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 637.65 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 3624.5833 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 77.35 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 490.9667 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 113.75 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 91 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 481 | 13 | 1 | 2 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 19.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 361.4 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 523.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 886 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 120.25 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 644.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 638.94 | 13.8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 773.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 21970.6665 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 20040.2498 | 285 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168.9666 | 137 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8451.5167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13996.2666 | 163 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26342.1666 | 335 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66662.8328 | 830 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26840 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69324 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18943.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36348.4 | 121 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2915.9173 | 60.58 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25511.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120.6 | 402 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1729 | 190 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7503 | 610 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1647.8 | 132 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1015 | 35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6774.4998 | 510 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9740.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65502.35 | 881 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109263 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110074.9995 | 750 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21336.1664 | 409 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28608.333 | 500 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44669.4496 | 651 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46925.083 | 515 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53805.15 | 651 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67686.5 | 830 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167967.9994 | 870 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14630 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36960 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49850.6666 | 320 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1659.9667 | 19 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96236.4994 | 870 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3296.3329 | 620 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13208.3333 | 100 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.1331 | 392 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1584 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65306.6661 | 790 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1053.3333 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10989 | 330 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36135.833 | 515 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43113.4997 | 489 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233977.3328 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7381.5 | 1330 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31220.7999 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35555.7165 | 307 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 25490.4329 | 641 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1050.5 | 110 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 120277.6298 | 557.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27531 | 630 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1579.8666 | 136 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2478 | 60 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1942 | 40 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4272.1 | 42 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41063.4999 | 255 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9222.4998 | 510 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 119982.5497 | 831 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4188.2 | 86 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 65.8331 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 684 | 19 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2529.215 | 60.58 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54626.0831 | 565 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53780.1 | 758 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23620.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 186.6375 | 177.75 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9240 | 60 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 882.9333 | 14 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 535 | 107 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5556.8328 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26205.3331 | 634 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51701.2162 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14984.125 | 97.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94032.4997 | 870 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120646.1664 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20445 | 435 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6547.4997 | 405 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11040 | 115 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1350.9 | 237 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1274.7167 | 17 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19579.9999 | 330 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8373.75 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15505.6666 | 257 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34877.333 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14999.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 26755.2 | 557.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3343.0063 | 60.58 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49107.9163 | 565 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11482.6666 | 320 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21851.5 | 290 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3913.9996 | 570 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 874.9999 | 420 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4653 | 705 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 6351.0667 | 38 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 30796.8331 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1379.7 | 42 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7698.1665 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23296.7999 | 153 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23996.05 | 247 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54103.6329 | 614 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 38446.6665 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 65387.083 | 575 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 20054.055 | 567.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1918.91 | 47.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4815.9998 | 240 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13246.5666 | 77 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1581 | 620 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1567.0665 | 644 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4259.5 | 35 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17547.0166 | 121 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8118 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19622.1666 | 278 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38113.8331 | 637 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1003.8 | 42 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3924 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9280.8333 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49370.5329 | 626 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 338145.5 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4209.3328 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 23680.2098 | 557.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39972.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 487.5 | 32.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 44865 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3328.16 | 35.2 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 6911.6666 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 305.0666 | 35.2 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 106404.3331 | 610 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 27866.4166 | 335 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 5087.5332 | 268 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 80858.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 496.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 405 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 934.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1124.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1453.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3180.8333 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 362.645 | 18.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 878.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 185.25 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 542.595 | 18.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 557 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 580.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | NULL | NULL | 800 | Miscellaneous | NPCC | Winter | NULL | NULL | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 337.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 462.35 | 21 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 919.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 561.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 504.7 | 10.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 756.125 | 26.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 522.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Oil | OL | 800 | Miscellaneous | NPCC | Off-Peak | 722.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Winter | 11144.1 | 66 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 730 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 748.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 790.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 960.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1080.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 299 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1050 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 273 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 629 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 706 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 368 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1896.6666 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1900 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1233.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2322.8333 | 70 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | HRSG Boiler | HRSG Boiler Tube Leaks | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 5139.781 | 58.83 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2016 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 4422 | 26.8 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 862-CoG steam units
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.75 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 442 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132 | 66 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 665.4998 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2839 | 167 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.3333 | 52 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 839.9 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 912.1833 | 229 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 150 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.7 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.9 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 7 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 384 | 16 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 698.6666 | 80 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1242 | 207 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9360 | 600 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412.5 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 436.9167 | 5 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2783.3332 | 167 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.9667 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 271.6 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 939.3998 | 231 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1867.8833 | 37 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3378.9996 | 654 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 72886.4833 | 109 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668 | 167 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.8 | 16 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.9998 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 241.6667 | 25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 425.1 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9058.9333 | 46 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 4 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 835 | 167 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5139.9166 | 37 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 880.3166 | 221 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14808 | 240 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.2 | 9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.3333 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 654.0832 | 167 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 985.5998 | 462 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 471.9 | 18 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 44 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 32 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162 | 27 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 908 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.1667 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3600 | 180 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.95 | 39 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 908 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231 | 33 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121027.8328 | 830 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 3 | 5 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.6666 | 80 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 277.0833 | 5 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1667 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.7333 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.4 | 16 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1812.755 | 15.1 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9308.8333 | 202 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2234.4996 | 654 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14875.9999 | 240 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.1667 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.0999 | 129 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 331.1 | 14 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 356.8 | 16 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.3333 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105.75 | 27 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 370 | 74 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1362 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 412.5 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28971.153 | 544.4 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1848 | 24 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 348 | 29 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7.8 | 13 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2536.2826 | 60.58 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 9149.54 | 8.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 4454.4 | 11.6 | 1 | 1 | 1105-Generating tubes | D2-Forced - Delayed | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 1944 | 9.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 8421.84 | 12.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 8665.91 | 6.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 1012.8 | 9.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.1333 | 61 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.5 | 87 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 627.8556 | 50.77 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3707.0833 | 205 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3851.9833 | 47.95 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 405.8333 | 5 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 790.6 | 59 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 175.8333 | 10 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.3 | 83 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.25 | 87 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.8 | 84 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 673.3333 | 20 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1113 | 105 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 4488.5765 | 37.41 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 277.59 | 97.4 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1610 | 23 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 117 | 3 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1 | 1 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 25643.9999 | 180 | 1 | 1 | 1120-Convection pass wall | U2-Forced - Delayed | 650-Fluidized Bed
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.0833 | 95 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.7667 | 9.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9532 | 40 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2112.8731 | 70.39 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39016.3331 | 670 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2197.25 | 47 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.7083 | 9.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 698.25 | 285 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 742.5 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1962.6 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2423.2125 | 42.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2740.3665 | 458 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2806.3 | 38 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3244.6667 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5825.5167 | 23 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15981.2666 | 53 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 223.8 | 36 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 377.7165 | 51.39 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 384.3813 | 20.74 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23442.3207 | 497.89 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Winter | 5019.2999 | 162 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4816.35 | 417 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.5 | 30 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1259.225 | 28.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19021.7666 | 43 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1285.7093 | 46.64 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43735.9999 | 330 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1556.4833 | 47 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153.9792 | 23.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 361 | 9.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 901.3125 | 42.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 526.7518 | 70.39 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2499.1267 | 46.64 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2266.9667 | 47 | 1 | 1 | 1140-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1179.7 | 47 | 1 | 1 | 1140-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23216.9 | 42 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 212.0083 | 61.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1059.5666 | 33.25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 98921.2 | 49 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.046 | 22.89 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3014.2666 | 37 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2332.0125 | 42.75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5890.8333 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.5 | 30 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2006.1167 | 47 | 1 | 1 | 1140-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 591.25 | 215 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1200 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.8333 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 262.2 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858.6666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1106.0667 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8981.1333 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.5 | 70 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1365 | 65 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1464.5 | 202 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1510.4999 | 171 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.85 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 217.5333 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 295.3999 | 84 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 599.7333 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1174.15 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2141.0666 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 529 | 92 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6738.6667 | 32 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1617 | 385 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.6666 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162 | 54 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.3333 | 172 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 231.3 | 54 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280.5333 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308 | 112 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 346.5666 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391.4666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 438.5666 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 520.3333 | 70 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 557.8666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 673.4 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 711.9 | 54 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 759.4999 | 186 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 800.8 | 56 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 890.8666 | 83 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 922.3666 | 67 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 977.5 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1490.9998 | 252 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1802.25 | 267 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.1 | 42 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.15 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.6 | 39 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258.5333 | 56 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 398.95 | 79 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 593.75 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 876.3 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2272.4833 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2333.8666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2638.1 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3104 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.3333 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695.5 | 107 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3667 | 386 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1261.8333 | 67 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.3333 | 10 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.3333 | 67 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.6 | 42 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 254.15 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 276.3166 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1020 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1262.7333 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1992.5333 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2025.1333 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10589.5166 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88881.4 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 512.3333 | 106 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39523 | 60 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1606.0487 | 21.64 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.7499 | 117 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.6666 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 853.6666 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1539 | 108 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.9333 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.8 | 42 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.5 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 277.75 | 55 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 282.6666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 394 | 197 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 489.6333 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 823.53 | 84.9 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1000.2333 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1183.6167 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1233.1 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1721.9999 | 252 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2346.0666 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10483.1666 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1218.0833 | 47 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.6666 | 124 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 167 | 167 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244 | 122 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8 | 72 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.8666 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.8 | 72 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275.9 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 476.8 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 495.4165 | 205 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 514.3 | 74 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 604.8 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 684.6666 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 744 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1025.0666 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1035.45 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1441.6333 | 61 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2099.2 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10156.85 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28806.85 | 57 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304 | 152 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508.5 | 27 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1188.3333 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.9333 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.4 | 72 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.2 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 257.3 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 338.0667 | 44 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 426.6666 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 744.05 | 69 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 931.2 | 64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1006.2 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1078.7166 | 59 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8255.4999 | 237 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.25 | 47 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1930.5 | 117 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8124.8666 | 107 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 12767.7 | 66 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6963.3667 | 22 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 399 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.75 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.3333 | 19 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 7 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3873.5833 | 235 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 971.6667 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1329.1667 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.5 | 39 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132.5 | 53 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 355.8333 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 556.9167 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.5833 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.3333 | 31 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 124.95 | 49 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.75 | 43 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 224.5 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 650.1666 | 94 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22686.4998 | 255 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 184.5833 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.25 | 45 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.5 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 520.5 | 15 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1200 | 200 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2140.0166 | 221 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65034.6662 | 670 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.6666 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17 | 3 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45 | 45 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419.05 | 17 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 884 | 26 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1280.4 | 66 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.9167 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 149.8333 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 183.8333 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6275.6333 | 59 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3333 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 45 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5152.6667 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5550 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5620 | 75 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40593.25 | 409 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 166.25 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5688 | 24 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 30 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1393 | 140 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339.25 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1839 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.5 | 15 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13 | 30 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 535.2666 | 124 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44089.1664 | 382 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.75 | 15 | 1 | 2 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1236 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1160.85 | 81.75 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192 | 10 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.75 | 21 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 734 | 60 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18414.9999 | 150 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102.6666 | 77 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1161.0667 | 8 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.5 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.0833 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.8333 | 10 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2 | 9 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1667 | 5 | 1 | 2 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 287.75 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3531.65 | 83 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.58333 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5833 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1600.25 | 86.5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3793.125 | 72.25 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4249.05 | 13 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 209.85 | 9 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.99999 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.25 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140.625 | 67.5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 685.3375 | 81.75 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1658.5 | 62 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2058.75 | 67.5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.95 | 9 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.66666 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 201.4833 | 77 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.6666 | 92 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.3333 | 115 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1077.25 | 139 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184.7833 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1531.8833 | 107 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4908.3333 | 124 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9973.3333 | 187 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.6666 | 94 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3999.6666 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6150.9 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14624.1666 | 70 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184 | 92 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.75 | 77 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2773.8 | 92 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3709.2 | 66 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 16 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150.3333 | 82 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 954.5 | 46 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2257 | 122 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 486.5 | 139 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1437.9166 | 85 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1444.6667 | 22 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2416.8 | 144 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2110.5 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2600.9166 | 59 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2639 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8685.3 | 262 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 75.8333 | 175 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176177.3331 | 577 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222.25 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1749.3 | 42 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1993.8166 | 227 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4276.0666 | 77 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8974.5 | 62 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.3333 | 80 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112 | 140 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235.3333 | 40 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288.1666 | 130 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 521.25 | 45 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 621.6 | 8 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1796.8999 | 102 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4311.3333 | 116 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10008.6833 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1155.6 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1691.9166 | 79 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2324 | 83 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23365.5 | 111 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470.25 | 57 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 583.2666 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.4999 | 150 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75.8333 | 26 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.75 | 115 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.3333 | 110 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.9666 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 501.1666 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 592 | 160 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2203.4166 | 137 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4546.6666 | 62 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42812.5666 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 388 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 683.1 | 66 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695.1666 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 956.4 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2889.25 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5582.75 | 137 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 608 | 19 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1262.7333 | 47 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 8 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.2498 | 267 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290 | 145 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 626.65 | 83 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 895.3333 | 68 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1071 | 102 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1471.7666 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8174.5666 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9078.8333 | 47 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9429.1666 | 73 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10193.1 | 122 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15261.3333 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 217.6 | 102 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.65 | 33 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1027.5 | 45 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2009.15 | 33 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3468.5833 | 107 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7938 | 98 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8583.9999 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9266.95 | 83 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16097.85 | 83 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 569.3333 | 122 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1943 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14851.2 | 96 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17081.5 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 81 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 218.75 | 75 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 516.0833 | 55 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1229.05 | 47 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18263.75 | 95 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.9666 | 142 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.9999 | 150 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 513 | 60 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4219.5 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164 | 82 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2597.3166 | 103 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2926 | 120 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3991.2 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 3647.2 | 47 | 1 | 1 | 1180-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1001.1 | 47 | 1 | 1 | 1180-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 2 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.4167 | 1 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.5 | 63 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.9166 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1100.6666 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4719.75 | 93 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16020 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2156.6333 | 97 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3068.5 | 51 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3301.3333 | 80 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33256.3333 | 89 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 384.9999 | 132 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 632.8833 | 127 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1518.6666 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1966.0666 | 77 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 52.5 | 150 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 3375.6665 | 190 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.7166 | 59 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.4166 | 137 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 383.0666 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5385.3166 | 83 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.75 | 41 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55 | 110 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 396 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671.1166 | 67 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 904.8 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2080.8666 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3605.8 | 121 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4082.2333 | 103 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9360 | 72 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9497.4999 | 87 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11342.6666 | 94 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.3333 | 52 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1254.3332 | 212 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2056.4 | 212 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39530 | 590 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | HRSG Boiler | HRSG Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 1946.56 | 60.83 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 850-Combined Cycle Block
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186.2667 | 4 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 220 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.5 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.9999 | 90 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.55 | 2.55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 433.55 | 87 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1020 | 68 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2480.8666 | 68 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 98.6833 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1881 | 228 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 868.3133 | 60.58 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10404.7167 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150.6667 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3616.65 | 141 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49450.6666 | 76 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.0833 | 65 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 285.7333 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1960 | 280 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5847.3998 | 507 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 409.9331 | 559 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.75 | 3 | 2 | 2 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7427.1 | 19 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.2 | 6 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 811.3333 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1249.25 | 3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1696.5166 | 137 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1392 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2438.2 | 167 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.1333 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 174.2667 | 8 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 373.9422 | 2.63 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 892 | 223 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 793.6 | 4.96 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1618.1665 | 365 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 557.7498 | 291 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 12.9166 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1333.8 | 247 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3640 | 280 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 501.8043 | 60.58 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2835 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3660 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.8333 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 113.1167 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4827.75 | 471 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5756.8333 | 130 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17417.7 | 81 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.84 | 1.61 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.3333 | 100 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 185.4999 | 105 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1487.9667 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1506 | 6 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8466.55 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 745.9667 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1218 | 280 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2520 | 280 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1804.2282 | 137.03 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 203.25 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25403.4 | 44 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 807.8 | 6 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 855 | 57 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 187.2 | 2.6 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1871.5833 | 37 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7331.6664 | 830 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.2333 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.2 | 52 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 399.4333 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.0667 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 247.35 | 51 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501 | 167 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 817.5 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1546.125 | 6.65 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2583 | 287 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 1.5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 625.65 | 2.91 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 811.8166 | 67 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1186.25 | 365 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 790 | 316 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 57.5 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2766.3999 | 228 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1472 | 8 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6306.05 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111.6833 | 1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.75 | 11 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 139.7 | 3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 263.8 | 3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 372.48 | 1.94 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 405.85 | 3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 581 | 166 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8556 | 276 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 299.25 | 105 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4535.5 | 193 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 997.5 | 266 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10051.35 | 593 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11905.6231 | 137.03 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 790.0666 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 465 | 10 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 178.88 | 3.2 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 2377.5467 | 3.2 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 56.73 | 9.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 234 | 39 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 857.5 | 49 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1860.9066 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1565.2266 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1620.3733 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 3206.72 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1537.0666 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1825.12 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U1-Forced - Immediate | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1283.04 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1103.6667 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 866.25 | 275 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1798 | 310 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1875.5 | 310 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3103 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1963.3332 | 310 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2240 | 280 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2387 | 310 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30577.3333 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1953 | 310 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2140.0831 | 305 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1439.9999 | 270 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.75 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23272.3333 | 220 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1943 | 290 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 295.8 | 116 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3082.2 | 99 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 509.8333 | 115 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1771.2 | 123 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231.4333 | 53 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 477.9833 | 119 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 239.8 | 109 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1519.4333 | 79 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 12690.8333 | 97 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | U1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Summer | 9127.1332 | 158 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | U3-Forced - Postponed | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296 | 74 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184.1666 | 65 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 127.9333 | 101 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2016 | Coal | LI | 100 | Fossil-Steam | NPCC | Off-Peak | 17230.2999 | 159 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 450 | 45 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 275.7 | 18 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 327.6 | 18 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48887.6662 | 670 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15097.485 | 542.1 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72556.7331 | 607 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.1667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2025 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2030 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3445.5 | 45 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 755.55 | 109.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.6667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.1 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115.7333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123.2 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.5333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 206.2667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 293.7667 | 14 | 1 | 7 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1429 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4762.5 | 95.25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13380 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1942.25 | 114.25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5980.8661 | 871 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 692252.1665 | 455 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 7617.7333 | 97 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4885.4916 | 90.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9249.1 | 42 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 941.3333 | 20 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1373.4291 | 85.75 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5229.9333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5940.9 | 138 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124 | 124 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 246 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1362.6667 | 16 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7165.6666 | 185 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8227.9583 | 90.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 114 | 57 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1739.1 | 62 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51244.8327 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4285.6666 | 215 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10832.4166 | 215 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1136.1 | 42 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1616 | 30 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3324.3 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192 | 8 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 686.6667 | 20 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.93332 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.2 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.5 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.1 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 134.8667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 275 | 110 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.1 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 322 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 963 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1118 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1439 | 60 | 1 | 41 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1512.3333 | 26 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6115.05 | 321 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9176 | 62 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40423.2164 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | SF-Startup Failure | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95794.0664 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 257207.95 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56281.2164 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 424.6667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2315.1333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14 | 14 | 1 | 8 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 757 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1008 | 21 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2976 | 4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 525 | 4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2810.3833 | 91 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4286.25 | 95.25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34021.2827 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.5 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3381.3 | 221 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5172.6997 | 519 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9583.3333 | 50 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.2 | 24 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.3333 | 40 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.9667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.3333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 332 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 344.1667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 523 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5189.3041 | 85.75 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 877.0833 | 62.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1201.2666 | 37 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D3-Forced - Postponed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6669.1667 | 50 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.5667 | 17 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.3333 | 119 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.525 | 128.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196 | 15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1086.3667 | 23 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.2 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 516 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3546.0332 | 418 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 696.2667 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1320 | 55 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2663.25 | 45 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2986.2 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21333.75 | 45 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.1667 | 10 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 735 | 70 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.8333 | 70 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41.3 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115.0333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.6666 | 104 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 256.4333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 335.7667 | 14 | 1 | 11 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 642 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 685 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1066 | 410 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2058 | 85.75 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6380 | 220 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2884 | 4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2880 | 4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2976 | 4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.5 | 30 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3012.1 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4512 | 47 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 364.55 | 23 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 942.5 | 30 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2160 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5316.85 | 33 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.7667 | 14 | 1 | 2 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.8 | 16 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.4333 | 14 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 232 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 257 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 292 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 512.8 | 16 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 736 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 180120.45 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 210382.8 | 881 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7875.9999 | 264 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2365 | 25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1190.4166 | 25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 785.1667 | 35 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D2 | Forced - Delayed | 2016 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 651.78 | 42.6 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | TRE | Summer | 1692.4833 | 163 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 852 | CC steam units | TRE | Summer | 277830 | 105 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 852-CC steam units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 3809.7 | 51 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 860-Co-generator Block
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 603.6 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5472.4 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4024.9998 | 345 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2058.3333 | 65 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 806 | 104 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704.4 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1030.8 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1820 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 701.2 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4018.8 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7924 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1284.4 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1605.6 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14814.4 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 5399.3333 | 104 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 508.4 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4404 | 24 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1834.3 | 49.8 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 292.2833 | 71 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4387.5 | 78 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3812.25 | 195 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5452.6832 | 257 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 19379.95 | 347 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 9347.1832 | 233 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Gas | GG | 851 | CC GT units | RFC | Winter | 1092 | 104 | 2 | 2 | 1360-Boiler drains system | D1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 3.8666 | 58 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2280 | 114 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2016 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 693 | 66 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2016 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 1491.8666 | 26.8 | 1 | 1 | 1360-Boiler drains system | U2-Forced - Delayed | 862-CoG steam units
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9999 | 234 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.55 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.8 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.1667 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.8 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.5 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375.4 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 658 | 84 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3532.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5194.6666 | 320 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.3 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 240 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3243.6 | 204 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 166.9982 | 182.18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26731.5 | 355 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 7 | 1 | 2 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169.5833 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 58.3 | 106 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1100 | 275 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.9167 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.7 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.6 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301.8 | 18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1970.8333 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2581 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15340.5 | 315 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22274.25 | 255 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91 | 91 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 981.4666 | 136 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3432.6665 | 542 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 125.6233 | 16.9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156 | 40 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220 | 20 | 1 | 2 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 45 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308.3333 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357 | 30 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1474 | 60 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 966.7831 | 817 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1309.6064 | 372.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276.25 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 532.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 872.6667 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 7434.9599 | 187.2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3910.863 | 192.18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25 | 10 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 223.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 281.25 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 459.1666 | 58 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1000 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1190.6665 | 470 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1034.9999 | 310.5 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1932.6663 | 520 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33000.4 | 844 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 200.6666 | 172 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1020.6999 | 354 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2755.9329 | 617 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9758 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182531.8 | 319 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.7 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.75 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.6 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2143.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6681.6666 | 95 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15150.9332 | 268 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22333.7499 | 255 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.7266 | 66.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 186.2 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1047.9997 | 393 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 33.215 | 21.9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 280 | 200 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1058.9999 | 180 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3045 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 275.625 | 367.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 2 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5793.7333 | 76 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.6 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.2333 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.4 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.5 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174.1164 | 337 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 241.5 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.3333 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 518.7 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1431.3331 | 380 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2004.1663 | 481 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2446.5498 | 501 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.1664 | 415 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 424.1667 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 617.5167 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 30668.33 | 7.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 278.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 25 | 1 | 3 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286.9425 | 127.53 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1393.2 | 108 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1173 | 230 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 950.7766 | 48.1 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 580.7499 | 345 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1808.9166 | 245 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34720 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37072 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.5 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.9167 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.3167 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.1 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630.6667 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1153.3333 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1620.6664 | 340 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 13.25 | 7.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 129.7333 | 56 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1450.959 | 192.18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2700 | 150 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4380 | 240 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 11 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.3333 | 20 | 1 | 3 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 20 | 1 | 4 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39814.0664 | 436 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5259.8 | 78 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 705 | 705 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 52.5 | 70 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 794.4364 | 333.33 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.5 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.9 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.3833 | 103 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.6667 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228.6667 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.7333 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 554.2167 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 792 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 927.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1089.3332 | 304 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1742.9999 | 315 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 494.88 | 412.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1013.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1200.0098 | 331.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 937.5 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3244.3499 | 387 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 104792.4333 | 86 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 82.1667 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 10 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154.1667 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 539 | 49 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3825.8 | 517 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27151.1332 | 511 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196 | 140 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1632 | 408 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3822.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6789 | 109.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7149.9166 | 103 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.6833 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.75 | 45 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.6833 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.4167 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.65 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 20 | 1 | 2 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.4 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.9167 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.5 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.8 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 324.6833 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 489.2166 | 197 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 786.2 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1258.0664 | 334 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3277.5 | 345 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11550.72 | 180.48 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 203.3925 | 17.31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 10.85 | 10.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 310.2 | 18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1425 | 150 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18970.8331 | 290 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 28.2333 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 32 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 10 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.5 | 15 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.75 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 341.6667 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 215311.5 | 270 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20070.9664 | 737 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 35370 | 108 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 320655.1666 | 118 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2.5 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 0 | 118 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 850-Combined Cycle Block
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1023.75 | 117 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 273.3333 | 82 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 438.6665 | 280 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 473.2083 | 102.5 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2116.5 | 415 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 404.7 | 71 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3332 | 200 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1795.5 | 630 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.6666 | 103 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5761.5 | 345 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 770.5049 | 298.26 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9923.7995 | 708 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12905.9997 | 405 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.2546 | 58.13 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 169.84 | 77.2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.206 | 71.88 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.38 | 71.88 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.5333 | 32 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 930 | 100 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8011.6664 | 460 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 934.8 | 328 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 753.5 | 11 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 52.5 | 90 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2906.1665 | 470 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 687.083 | 485 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1183.6666 | 106 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 160 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 176.6666 | 106 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6192.9998 | 330 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.6667 | 22 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3503.4667 | 32 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3989.3331 | 320 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.5 | 105 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.3333 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 560.9999 | 153 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2349.7665 | 449 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55.7333 | 44 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7344.75 | 9 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 211.4165 | 295 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 565.44 | 68.4 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1888.6 | 71 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.3333 | 115 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 344.1666 | 118 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5525.333 | 518 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18903.75 | 355 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.5 | 178 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8414.1665 | 575 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.4165 | 277 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262 | 262 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18062.0831 | 335 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4151.933 | 434 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206 | 412 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.9999 | 120 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 355 | 355 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 737.5 | 50 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 929.28 | 96.8 | 1 | 1 | 1407-Forced draft fan lubrication system | D2-Forced - Delayed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23379.5328 | 842 | 1 | 1 | 1407-Forced draft fan lubrication system | U3-Forced - Postponed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 966 | 276 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 130 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1016.6666 | 200 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 882 | 294 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 30489.3333 | 130 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3791.7332 | 472 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5927.8 | 428 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 305.5 | 235 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 821.3332 | 385 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 506.3332 | 245 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11085.9998 | 723 | 1 | 1 | 1407-Forced draft fan lubrication system | U2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2060.7997 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26112 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16625.6999 | 378 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 906.6666 | 160 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1118.5832 | 155 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 186.6667 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 512.5 | 30 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 746.5 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3044 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 12049.8 | 151 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 130296 | 183 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 74.5 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 224.8333 | 19 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 625 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 130.9833 | 29 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8454.3997 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23196.3331 | 404 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29414.4 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 303.7333 | 42.88 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4785.4 | 337 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5295.4999 | 267 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6924.7833 | 163 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3982.4999 | 405 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18167.5664 | 454 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 29.1667 | 35 | 1 | 2 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 106.3333 | 5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 131.25 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 208.3333 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 275 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 303.5 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 342.3333 | 13 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 605.8333 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 941.6667 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1154.1666 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4079 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1039.8332 | 170 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73068.5 | 634 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120473.5999 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3376.7831 | 383 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.1666 | 65 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480.1664 | 430 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2041.6665 | 250 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12822.6666 | 163 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 255.8333 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1715 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 286.5 | 30 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 241.6667 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19320.5333 | 64 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6325 | 575 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1172.5 | 67 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2873 | 442 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82491.7499 | 405 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 839.5 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2782.2666 | 216.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 570.0167 | 23 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 329.5833 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2948.75 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 56619 | 243 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.6 | 42 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53290.6666 | 320 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 23103.4 | 71 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7430.4 | 344 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 614.8332 | 155 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 963.0332 | 173 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3452.8666 | 151 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3744 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5171.8798 | 296.1 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 68.8 | 24 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 10 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 65 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 68.3333 | 5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 827.5 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 33540.5 | 49 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 154280.7 | 243 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2100.6665 | 184 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253.4 | 362 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 480 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 868.75 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1260 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 76 | 30 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 519.6667 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 761.6667 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 957.3333 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1392.4166 | 245 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 162.9333 | 104 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.1667 | 29 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57856.7 | 353 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 13.75 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 350 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 431.3333 | 5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 486.75 | 165 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 855.8333 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 931.5833 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2293.5 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3260.25 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5068.75 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 52524.75 | 356.1 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 136.25 | 75 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 253.4 | 28 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 253.8667 | 32 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 350.35 | 33 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 614 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 165 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 16905.0999 | 213 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11787.183 | 497 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3470.1328 | 728 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2903.25 | 245 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4015.9999 | 240 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4432.9 | 97 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 908.7997 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7411.2 | 384 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5575.5 | 378 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11179.7166 | 107 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1430 | 100 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16758 | 84 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7.75 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 198.3333 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 537.5 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 565 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2396.35 | 33 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11.25 | 5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 116 | 10 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 122.5 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2216.6667 | 35 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19889.0998 | 594 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21162.5332 | 307 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91579.5163 | 577 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 68904 | 528 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 6005.1 | 222 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 5050.1333 | 136 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1485 | 55 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 800-Miscellaneous
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 341.4166 | 85 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10162.5331 | 338 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 928 | 580 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 680 | 272 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 43.9998 | 528 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 181.5 | 165 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3299.1664 | 370 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 83.4166 | 143 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4200 | 70 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 376.6666 | 100 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.4 | 8.4 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157.5832 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 219.0453 | 21.44 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 746.075 | 16.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 241.5 | 105 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2908.3333 | 125 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2279.8266 | 104.9 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 522 | 52.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.775 | 155.1 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.43 | 123.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 561.56 | 111.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 745.0033 | 210.85 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22531.8332 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 728.5 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1088.6666 | 230 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 622.8866 | 93.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 841.4166 | 87.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2299.7332 | 448 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 595.5566 | 95.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.165 | 140.1 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 271.695 | 92.1 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 809.825 | 111.7 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.8332 | 155 | 1 | 2 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 15 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 926.4 | 193 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11063.1833 | 43 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6451.6666 | 245 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 291.9166 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 866.2665 | 178 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 467.4999 | 165 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 940.3333 | 65 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.16 | 5.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1160.8317 | 16.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5894 | 842 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1390.6665 | 560 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1560 | 600 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43.0833 | 235 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.1666 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1785 | 595 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 131.25 | 105 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.42 | 140.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 748.65 | 93 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 207.0005 | 104.37 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 845.5831 | 365 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 310 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16357.6666 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 958.7999 | 153 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.92 | 144.1 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5599.3 | 842 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14159.25 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 206.6666 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14037.3332 | 280 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 764.6666 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 18.2 | 19.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 295.8333 | 125 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.8 | 65.4 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1305.7916 | 323.75 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2348.115 | 96.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2976.6666 | 200 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 147.004 | 133.64 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4792.3333 | 11 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7721.5832 | 155 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 14.95 | 13 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483.425 | 158.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 476.0665 | 193 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1720.9165 | 193 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 412.9832 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1872.9664 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 587.4832 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7340.8331 | 766 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3909.9998 | 276 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17904.5332 | 142.25 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7814.1667 | 50 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 260.6664 | 391 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 351.9998 | 480 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2379.1665 | 250 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.4166 | 55 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1756.6666 | 136 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1169.133 | 494 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1547.9999 | 216 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 922.5 | 102.5 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 592 | 370 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13128.4999 | 231 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2661.6 | 88.72 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4575.45 | 517 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12748.7498 | 525 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 3409.1799 | 377.4 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 503.7499 | 195 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6077.7331 | 577 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 217.4999 | 90 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1543.5331 | 338 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.8515 | 3.13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1507.8775 | 3.13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1687.1667 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3192.744 | 140.96 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 569.6 | 71.2 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1769.6999 | 306 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.8333 | 175 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4692.9998 | 570 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2865.4165 | 325 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3671.75 | 95 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.5026 | 55.66 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1.1667 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1144.933 | 554 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.5 | 31 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6077.5 | 325 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 186.9 | 178 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 944.5333 | 23 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.9333 | 61 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2752.208 | 185.96 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4936.134 | 75.96 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5021.333 | 560 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.752 | 57.66 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 446.3999 | 216 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 676 | 169 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 753.3332 | 400 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3762 | 440 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.3333 | 25 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126.975 | 169.3 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2588.34 | 72.3 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1057.6666 | 167 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 201.4999 | 195 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 967.8 | 96.78 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.6666 | 136 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1396.5 | 13.3 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3524.4998 | 570 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 794.733 | 524 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 327.6 | 108 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 91.2499 | 75 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 4082.4999 | 345 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 405 | 108 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.6 | 126 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1842.4999 | 330 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6148 | 424 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 480 | 1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 216.4166 | 49 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2768.1166 | 270.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 498.3332 | 325 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2439.5 | 70 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2640 | 330 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.1667 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 327 | 12 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 353.0333 | 178 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 704.8666 | 218 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1003.3333 | 28 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3842.0833 | 5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 6 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7496.8497 | 477 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1517.2498 | 315 | 1 | 1 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.75 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 289.9998 | 300 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.2082 | 24.41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.3333 | 34 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 35 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 30880 | 16 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12260 | 16 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 148.8333 | 235 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8295.6661 | 820 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.25 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 331 | 165.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2315.9999 | 180 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.75 | 19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 380.9585 | 37.41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 0 | 0 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3789.5 | 55 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26613 | 27 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2230.6665 | 280 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65943.5 | 105 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2 | 16 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213.8999 | 207 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2906.7499 | 165 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3310 | 331 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16066.5 | 9 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 285 | 570 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 657.0832 | 475 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8060.5 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4170.6666 | 230 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.5 | 90 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.3333 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 272.3332 | 430 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1092.8666 | 338 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3240 | 480 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81 | 12 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 565.5 | 174 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 614.0332 | 218 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3752.84 | 412.4 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 694.8 | 27 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1410.3833 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2532.25 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2125 | 340 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.5 | 90 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.9993 | 35.51 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 757.3332 | 355 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39983.9998 | 306 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 23.1466 | 49.6 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 332.5 | 175 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1899 | 211 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15793.5999 | 96 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2881.6663 | 475 | 1 | 1 | 1420-Other forced draft fan problems | U2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.5717 | 24.41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.0667 | 16 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 296.9833 | 103 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1108 | 8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4831.8666 | 248 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 4.8 | 1.2 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 8.4 | 1.2 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 7.2 | 1.2 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 87.6667 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 150 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 751 | 75.1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 850-Combined Cycle Block
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 881.6666 | 230 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 6493.85 | 33 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1357.4997 | 450 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 345.95 | 33 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 1014.6986 | 29.44 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 10.879 | 5.06 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 232.3767 | 16.1 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 63.0666 | 43 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 9.8 | 12 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 282.9 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.9166 | 175 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 829.035 | 204.7 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1102.3999 | 156 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 56.65 | 10.3 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 39 | 10 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 270.8 | 24 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270.6666 | 140 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 922.4665 | 202 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1650.05 | 61 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D2-Forced - Delayed | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 853.4 | 502 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130.7 | 26.14 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.55 | 33 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.739 | 5.13 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 413.1666 | 67 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 650-Fluidized Bed
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 260.1833 | 67 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 787.4 | 31 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1382.5 | 75 | 1 | 1 | 1430-Air supply ducts from FD fan | D2-Forced - Delayed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6638.9666 | 151 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 97.8033 | 48.1 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 140417.7663 | 502 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12402.9166 | 85 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 181880.6664 | 692 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 138404.0333 | 46 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 153.6999 | 87 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30422.3996 | 576 | 1 | 1 | 1430-Air supply ducts from FD fan | U2-Forced - Delayed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8111.6666 | 155 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | OS | 650 | Fluidized Bed | WECC | Off-Peak | 168.95 | 13.08 | 1 | 1 | 1430-Air supply ducts from FD fan | D2-Forced - Delayed | 650-Fluidized Bed
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435 | 87 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3974 | 30 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 701.5 | 230 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616 | 30 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3145.8167 | 11 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 5.635 | 4.9 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075.9 | 50.75 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 774.2498 | 285 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6840.9832 | 307 | 1 | 1 | 1431-Air supply dampers from FD fan | U2-Forced - Delayed | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 799 | 170 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 513.2165 | 581 | 1 | 1 | 1431-Air supply dampers from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.7 | 154 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61315.0997 | 462 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1692.0832 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 30345.4833 | 157 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11776 | 320 | 1 | 1 | 1432-Air supply duct expansion joints | SF-Startup Failure | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36981.3331 | 320 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34380 | 180 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5710.5653 | 141.76 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 28623 | 420 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28574 | 157 | 1 | 1 | 1432-Air supply duct expansion joints | D3-Forced - Postponed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9448.5666 | 163 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4381.3332 | 212 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 116.8333 | 140.2 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1482.7626 | 100.64 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3937 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 6681.2916 | 102.5 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 249.6666 | 70 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 224.2 | 59 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 593.0666 | 128 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1562.8666 | 119 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.5166 | 73 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 280.5 | 85 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1642.68 | 315.9 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29684.25 | 395 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1085.5 | 65 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 801.4499 | 351 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 4152.6997 | 786 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18078.5 | 30 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 169.1666 | 70 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1593.1999 | 84 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1370.4165 | 253 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 339.1666 | 110 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 858.4665 | 316 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 690.2998 | 351 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.8333 | 70 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.3332 | 170 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 1933.8 | 293 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.2 | 24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47 | 47 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158.65 | 19 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128.4666 | 188 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1037 | 61 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4582.5 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4414.2833 | 29 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14968.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 18401 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2766 | 461 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.25 | 175 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 262.7 | 74 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 342 | 19 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 32.64 | 4.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 647.55 | 27 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5023.4999 | 90 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.3195 | 2.13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175.4333 | 19 | 2 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1354.1666 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 298.6049 | 210.78 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 34.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2.8 | 21 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.1666 | 25 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 10 | 1 | 1 | 1450-Other air supply problems | D3-Forced - Postponed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5524.32 | 812.4 | 1 | 1 | 1450-Other air supply problems | SF-Startup Failure | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 512.05 | 539 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.1667 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65333.3331 | 320 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11806 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6291 | 466 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 77083.1332 | 292 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 90.7833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750.8466 | 336.2 | 1 | 1 | 1450-Other air supply problems | SF-Startup Failure | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 88.3333 | 106 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1089.9999 | 300 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 187.2666 | 106 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 447.5333 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 938.1166 | 43 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1150 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 56.7167 | 8.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1925.6665 | 530 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 97.1666 | 106 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.5833 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 685.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 848.25 | 261 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 385869.7499 | 315 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 149.75 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3367 | 8.2 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 90 | 75 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 47.4543 | 60.58 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.6666 | 82 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 718.25 | 221 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3286.3999 | 192 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1504.1666 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 278.75 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 279360.3499 | 159 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 11.9167 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.6667 | 20 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1393.3331 | 550 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 697.833 | 530 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6374.1996 | 609 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 344.5 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1128.8333 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 684.1333 | 14 | 2 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5028 | 4.13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.6666 | 160 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 42604.1329 | 692 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 905.76 | 100.64 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 90 | 6 | 1 | 5 | 1450-Other air supply problems | D1-Forced - Immediate | 800-Miscellaneous
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2647.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 800-Miscellaneous
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 39.5 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 800-Miscellaneous
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 74.5 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 800-Miscellaneous
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1441.0733 | 182.8 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 872.3 | 286 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1451 | Fluidized Air Fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2207.65 | 67 | 1 | 1 | 1451-Fluidized Air Fan | U1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.4667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.0417 | 38.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.5833 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.6083 | 66.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.4166 | 103 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.2 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 219.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 252 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.5 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280.5 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 301.3 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 356.25 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 364 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.5 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 581.9 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 602.6667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642.1166 | 59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 678.5625 | 57.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.3333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1243.6666 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1557.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1819 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1891 | 122 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1939.8332 | 206 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2051.75 | 87 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3352.5 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4098.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4139.7917 | 38.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6538 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7995 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8240.6166 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.9333 | 58 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.4 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.9999 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.9333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.3166 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.4 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6833 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.9 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.5 | 78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.1 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.4666 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.25 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.3 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.0667 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.7167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.0333 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.2 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222 | 111 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.2333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 248.5 | 71 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.3333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 359.0167 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 376.7833 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 383.0666 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 394.1666 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 463.6 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 479.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 511.5 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 512 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 513.6333 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 728.95 | 61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 740.25 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 741.4 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 863 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1070.8333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1094.1666 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1218.3333 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1265 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1275 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1283.3332 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1336.4833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1390.8 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1431.75 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1441.4333 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1578.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1580 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1851.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1915.6333 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2026.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2777.5 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3237.5 | 185 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4819.1 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15227.4999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.3333 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 203 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 331.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 594 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 638.5999 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1187.3332 | 274 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1305 | 174 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4341.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220.96 | 13.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 302.08 | 9.44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 349.14 | 10.58 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1008 | 252 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.8788 | 1.49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.1 | 2.22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.98 | 7.14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 213 | 17.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 176.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 767 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4039.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 6949.2497 | 399 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1188.6 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3756 | 313 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.1 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.18 | 1.48 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 176.4332 | 158 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136.9332 | 158 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1745.3332 | 280 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2001.6 | 417 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3544.5 | 510 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 535 | 107 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 967.7516 | 172.3 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.7 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.5833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.5 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.25 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.7333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176.6666 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 275 | 275 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.8 | 96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 363 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.3333 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.5 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420.9333 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.5 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 519.0667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 900.9 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1280.95 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1458.9167 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1495 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1500 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1739.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2475.3333 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3056 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3469.095 | 110.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3642.4999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5279.2667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5701.24 | 247.88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6804 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7100 | 355 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9129.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14400 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 9 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.5 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.35 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.4166 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.3333 | 62 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.55 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.1333 | 79 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.3 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.4 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.7333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.4 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.725 | 10.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.75 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.9 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193.2 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207.2 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 215.3333 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.6667 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230.7 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238.7667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 241.0667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 259.0667 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 301.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 303.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308.2666 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315.7 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 380.4167 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 383.4 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 392 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 413.5833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 425.25 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 435.9667 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 504.2925 | 224.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 546.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 591.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 637.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 644.7999 | 96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 673.8333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 702.65 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 712.25 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 730.7667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 819 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 912 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1006.3 | 58 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1133 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1379.5832 | 215 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1616.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4258.3333 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4319.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5211.8 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8010.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8428 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8680 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33588.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.5167 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.3333 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102 | 17 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.5833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 213.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 238 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 262.5833 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 300 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 336.4 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 544 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 659.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 843.75 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 980 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1079.8333 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1114.4 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1138.5833 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1267.75 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1427.25 | 173 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4510 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16820 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98 | 12.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 284 | 28.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 806.85 | 17.93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.96 | 8.12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1008 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 191.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 95.3333 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 59.85 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 209244 | 424 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 140 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28036 | 326 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435.7666 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1260 | 210 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.7355 | 74.99 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2437.9998 | 690 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2504.6664 | 340 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7608.2665 | 554 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 910.3165 | 193 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 132.275 | 48.1 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1 | 1 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.2 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 8 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46 | 8 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.75 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.75 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.5 | 155 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314.5 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345.6666 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 369 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 401.85 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451.25 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 468.7375 | 57.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 530.8333 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 627.25 | 48.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 757.5 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 828.75 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1116.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1171.3333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1631.8 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1937.5 | 62.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1990.15 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3182 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3306.9758 | 108.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7166.4833 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15045 | 102 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.0667 | 6.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.5333 | 79 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.2 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7666 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.25 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.8 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.2166 | 71 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.15 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.4999 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.5 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.4166 | 107 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.4 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.6666 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.0333 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 125.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.0667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.75 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 199.7499 | 255 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 233.8333 | 61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 253.2082 | 147.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 263.2 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 269.4667 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 311.7333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 427.0833 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 448.5 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.4999 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 502.25 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 522 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 584.8333 | 121 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 646.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 648 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 678.3 | 9.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680.4666 | 59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 704.7 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 726 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 807.5 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 874.6666 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 889.2 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 922.8 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 945 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 975 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 987 | 94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1022 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1080.9166 | 109 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1090.6667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1110 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1137.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1300.5 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1441.3832 | 439 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1787.4998 | 330 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1869.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1953 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2334.176 | 8.32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2720 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2795 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2822.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3141.6 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4183.2 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4544.25 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5250 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5255.55 | 153 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5709.1664 | 325 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5742.0333 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6391.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15992.0833 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.5 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.4 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.6 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.4833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.5333 | 97 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.0667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 542.3999 | 144 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 650.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 741.6 | 103 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1210.4167 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1278.3333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1729.4666 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8588 | 113 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 202.02 | 33.67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 279.9 | 9.33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2836.71 | 21.99 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.15 | 6.65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 87 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 396.06 | 17.22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 556.92 | 15.47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 99.2233 | 10.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 223463.9 | 583 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 493 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2448 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.575 | 7.65 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.5832 | 185 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 607.7499 | 165 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.16 | 61.8 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45871.1 | 446 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1168.375 | 97.5 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.6 | 29.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.0833 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.25 | 217 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.9167 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.75 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.3333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.375 | 23.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 282.9167 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 304.75 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 305.9333 | 176.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 385.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 413.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 464.6667 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 516.6667 | 38.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 561.0066 | 41.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 598.5 | 285 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 606.7333 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 667.3333 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 761.25 | 105 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 773.5 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 924 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 953.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 965.25 | 29.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1012.825 | 43.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1280 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1311.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1982.4999 | 78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2391.6665 | 350 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3080 | 400 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3710.1666 | 113 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3874.5833 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4782.6666 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7643.4375 | 38.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101380 | 370 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 3 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.5 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.35 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18.5 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.1 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.3333 | 94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.7333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.35 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.5666 | 79 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.5 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210.9333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 276 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 277.0833 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 281.25 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.0333 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 355 | 71 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360.4998 | 309 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 371.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424.6666 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 513.6666 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.2499 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 669.8 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 700 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 823.65 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 939 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1057.35 | 159 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1368 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1647 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2100 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4462.5 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4597.4333 | 214 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4667.5 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5275 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9759.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11180 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22319.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109420.2 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.5 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.7833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73.3332 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 112 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 188.6667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 484 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 702.1 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1032.2666 | 98 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1087.2 | 144 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1187.5 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2104.6664 | 328 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2860 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2896.7858 | 24.65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3960 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9393.0666 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 323 | 16.15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.78 | 3.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.6 | 2.95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 289 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 26834.9666 | 266 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27359.3667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 90.99 | 30.33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1685.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4536 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 486582.7166 | 277.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 20698.2664 | 424 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7544 | 328 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.8 | 6.6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1001.3317 | 10.3 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130 | 65 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5988.5 | 145 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 601.3333 | 80 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3949.6665 | 410 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 8735.3 | 21 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 173.16 | 48.1 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7 | 7 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.6333 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.75 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.25 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.4999 | 102 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223.6667 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.5 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.75 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 356.7666 | 278 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 372 | 8 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 405.1667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 526 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 546 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555.4166 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 590 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 602.95 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 671.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 856.8333 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 879 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1064.25 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1191 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1594.6666 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1902.5833 | 79 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2203 | 220.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3123.4666 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3250 | 62.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3513.3333 | 38.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3580.5 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 10316.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14406 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14710 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24175.3666 | 281 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.1166 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.9999 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.0333 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.2 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.3 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.4333 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.9166 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.4666 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.4333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.2333 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.2 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 173.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220.5 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 242.5 | 97 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 256 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.7 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 403.7499 | 255 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 420 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 466 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 478.3333 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 512.5 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 605.5833 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 654.15 | 63 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 712.3666 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 719.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 937.3332 | 152 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1062.6333 | 71 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1248.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1308.6333 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1501.6666 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1696.6333 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1913.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2553 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2913 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3087.5 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3848 | 78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17407.8665 | 286 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21527 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103721.9998 | 531 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160740.1331 | 317 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.25 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.3666 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.8333 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.9833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 315 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 318 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 344.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 348.8333 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 388.5 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 744 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 858.7 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 973.9333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4328.1333 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6790.6666 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33421.4999 | 270 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 406.98 | 67.83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.8292 | 8.35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.645 | 2.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.8 | 9.56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 128 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5320 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 52263.9331 | 589 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 949.8641 | 161.45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19057 | 323 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1170 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.1 | 2.9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 136 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 178.7499 | 195 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3686.0832 | 355 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 641.25 | 475 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1473.3332 | 340 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 62.4 | 48 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.2 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 8 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.7333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.3333 | 8 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.7499 | 86.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.8333 | 62.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.6666 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.7 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 309.3333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 696.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 711.9666 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 791 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 987.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1115 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1344 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1477.6666 | 62 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1634.1664 | 370 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1730.4 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2100 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2187.3333 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2466.6664 | 370 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3015 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3524.5 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3904.875 | 104.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 9 | 1 | 3 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.4499 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.1666 | 79 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.5333 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2333 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.05 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.1666 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.5 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.3 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.3167 | 8.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.3666 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.4667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.25 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.8 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.15 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.0333 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.5 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.75 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.3667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.5 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.3 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186.75 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.8333 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.5 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.1666 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.8 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 264 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 311.4833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 545.4167 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 830.9166 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 835.2 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 965.64 | 5.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1146.7333 | 103 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1233.1666 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1329.25 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1359.8331 | 410 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1470 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1564 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1848 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2445 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2507.5 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2550 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2786.4 | 108 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2920.3999 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3863 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3995 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4010.4166 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11100.4166 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14206.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145533 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.15 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.25 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.6 | 78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.1666 | 131 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 118.75 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 122.25 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.25 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.3667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 264 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 456.1333 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 470.1666 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 490 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 546 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6881.6 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8383.2667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40192.75 | 149 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 282.04 | 12.82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1623 | 270.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.9 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.92 | 7.99 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 290 | 290 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43894.0333 | 59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2844.6666 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 196.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 95407.0664 | 424 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1666 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 178.7499 | 165 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22755 | 185 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2275.6568 | 213.01 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 38.4 | 48 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.2667 | 24.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16.4 | 4.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.65 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.6667 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 115 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.4 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.8333 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.75 | 129 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 282 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.3333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 353.5 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 394.45 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 502.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 532 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 614 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 651 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 653.3333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 724.5 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 950 | 62.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 972.1667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 990 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1039.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1178 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1297.3499 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1305.6792 | 10.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1482.25 | 57.75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1730.0333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1893.3332 | 355 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2083.3333 | 62.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3323.6666 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3791.6666 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4203.75 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5328 | 108 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5836.6666 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7393.5 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11317.6665 | 380 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18056 | 296 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0833 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.25 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.8 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.9833 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.6 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.5 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.5166 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.8667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.5 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.8333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.8 | 7.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.25 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.275 | 4.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 55.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.65 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.75 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.4 | 137 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192.7333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200.4167 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 254.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276.6666 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 318.5 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 324 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 336 | 63 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 347 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 368.4 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 412.5 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.2667 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 455.0333 | 73 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 475.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 499.8667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 508.9 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 533.2 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589.5 | 131 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 644.4 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 650.1333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 660 | 66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 788 | 197 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 796 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 845.8333 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 917.3333 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 932.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1047.1833 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1153.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1427.0832 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1511.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1568 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1779.5166 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2201 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2306.3332 | 340 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2757.0832 | 325 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2895.3 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3462.8999 | 153 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4690 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.5 | 51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.5667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.6333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90.5 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103.2 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.25 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 151.2 | 168 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 249 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 308 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 319 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 343 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 477 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500.5 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 595.8332 | 143 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 598.02 | 99.67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.3 | 3.65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47613.8666 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 6400.6948 | 296.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9028.8 | 167.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18624.9166 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.4667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 18274.4 | 424 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 5559.3999 | 399 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 216.97 | 333.8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7661.76 | 69.4 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 312.5 | 75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2016 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2334.9 | 181 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3685.3348 | 510.67 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4281.3333 | 247 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15321.6662 | 634 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2016 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 23420.0896 | 557.4 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2016 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 25859.3331 | 395 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.4742 | 43.67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.2 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2016 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam