## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of DISTINCT_UNITS | Sum of EVENT_COUNT | Sum of MWLost | Sum of MWHrsLost
0020-Coal car dumpers; shakers; and unloaders | 3 | 3 | 48.3 | 1546.5116
0022-Unloading/receiving hopper (train/truck) | 1 | 1 | 13 | 9.75
0024-Rotary plow | 3 | 3 | 73.6 | 3094.9216
0026-Dust suppression system | 2 | 2 | 422 | 6428.4665
0028-Dust collection system | 10 | 10 | 2365.9 | 12238.5995
0030-Coal conveyors and feeders | 305 | 306 | 65545.29 | 915436.716
0035-Metal detector/collector (including magnetic separator) | 14 | 14 | 1433.58 | 8613.3798
0040-Coal elevators | 2 | 2 | 130.52 | 1714.6867
0050-Coal storage fires | 2 | 2 | 306 | 2591.7
0060-Coal crushers including motors | 20 | 20 | 2419 | 11627.6498
0075-Storage silos/hoppers | 35 | 35 | 3774.25 | 317240.8115
0080-Stackers/reclaimers | 37 | 37 | 2855.4 | 19145.216
0084-Coal conveyor scales-storage coal pile | 8 | 8 | 415.4 | 19649.8667
0085-Bunker feeder coal scales | 5 | 5 | 166.6 | 147.4566
0090-Bunker fires | 15 | 15 | 2469.49 | 18537.3849
0095-Bunker flow problems | 118 | 118 | 7623.2 | 93668.2633
0100-Bunker gates | 5 | 5 | 406.6 | 1531.6
0105-Bunker structures | 9 | 9 | 403.2 | 5721.5932
0106-Coal drying system (see additional codes 0125-0127) | 2 | 2 | 142 | 549.8333
0107-Screen (prior to bunkers) | 1 | 1 | 13 | 9.75
0110-Other coal fuel supply problems up through bunkers | 57 | 59 | 9403.34 | 81014.0361
0111-Solid fuel feeder conveyors | 74 | 75 | 2924.25 | 58738.1857
0114-Solid fuel volumetric feeder | 2 | 2 | 55.1 | 125.6967
0115-Solid fuel gravimetric feeder | 37 | 38 | 981.97 | 6514.7167
0116-Solid fuel feeder motors | 1 | 1 | 28 | 75.1333
0119-Solid fuel crushers | 1 | 1 | 32 | 368
0121-Other solid fuel feed problems | 19 | 19 | 674.27 | 7294.2954
0125-Coal crusher dryer hammers | 6 | 6 | 600 | 1650.033
0127-Other coal crusher dryer problems (see code 0106) | 10 | 10 | 845 | 14849.7498
0129-Other coal processing system problems | 73 | 77 | 8010 | 161278.7309
0131-Sorbent handling conveyors | 5 | 5 | 222 | 6005.8333
0132-Sorbent handling feeders | 3 | 3 | 174 | 318.4667
0155-Sorbent feed pneumatic transport system including piping and valves | 1 | 1 | 90 | 1080
0156-Other sorbent feed problems | 1 | 1 | 37.87 | 448.1283
0160-Bed material tanks/hoppers | 1 | 1 | 50 | 910.8333
0162-Bed material conveyors A | 2 | 2 | 64 | 1059
0163-Bed material feeders | 6 | 6 | 94 | 1427.0666
0200-Pulverizer exhauster fan (for indirect firing) | 33 | 33 | 2676 | 86079.1157
0205-Pulverizer exhauster fan drive | 5 | 5 | 436.53 | 8345.5137
0210-Pulverizer heater (for indirect firing) | 1 | 1 | 80 | 716
0240-Pulverized coal bin | 25 | 25 | 2594.88 | 38568.5148
0250-Pulverizer feeders | 1664 | 1668 | 169937.26 | 1136601.8791
0253-Pulverizer feeder motor | 50 | 50 | 5051.78 | 57375.8995
0255-Pulverizer feeder coal scales | 27 | 27 | 3785.33 | 60183.5238
0256-Seal air system (air to pulverizers) | 22 | 22 | 2967.13 | 16593.1203
0257-Coal Crusher/dryer between feeder and pulverizer | 16 | 16 | 2145.51 | 16010.1304
0260-Primary air fan | 194 | 194 | 29058.91 | 851381.8624
0262-Primary air fan lube oil system | 6 | 6 | 865 | 2220.3997
0263-Primary air fan drives | 70 | 70 | 10386 | 249894.8799
0264-Other primary air fan problems | 44 | 44 | 8641.8 | 89651.7055
0265-Primary air heater | 7 | 7 | 1928.81 | 46309.1901
0266-Primary air heater fouling | 13 | 13 | 1292.37 | 157525.1801
0267-Primary air flow instrumentation | 38 | 38 | 4242.2 | 42665.2016
0270-Primary air duct and dampers | 149 | 149 | 18840.74 | 298199.4874
0280-Pulverizer fires | 72 | 72 | 9712.46 | 151148.3033
0290-Pulverizer reduced capacity due to wear | 19 | 19 | 1567.1 | 34777.1168
0300-Pulverizer motors and drives | 167 | 167 | 16027.11 | 336487.9804
0310-Pulverizer mills | 943 | 948 | 102340.86 | 1934842.3607
0312-Pulverizer mill classifiers | 55 | 55 | 8269.1 | 82284.5249
0313-Pulverizer mill trunnion seals | 6 | 6 | 512 | 5797.8832
0315-Pulverizer mill coal level controls | 14 | 14 | 866 | 2502.3497
0320-Foreign object in Pulverizers mill | 155 | 155 | 10807.5 | 76440.0961
0325-Pulverizer skidding | 21 | 21 | 2184.35 | 21558.4788
0330-Pulverizer coal leak (pulverizers only) | 127 | 127 | 12602.13 | 85441.006
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 75 | 75 | 6052.22 | 36969.2073
0335-Pulverizer lube oil system | 203 | 203 | 19789.33 | 124942.7317
0338-Pulverizer control systems (temperature and pressure) | 51 | 51 | 6181.32 | 88779.8449
0339-Pulverizer System Puff | 50 | 50 | 4198.75 | 283151.2765
0340-Other pulverizer problems | 405 | 405 | 49360.4 | 712846.2206
0342-Pulverizer inert system | 6 | 6 | 1131 | 4864.866
0344-Pulverizer inspection | 94 | 95 | 8788.37 | 120076.1094
0345-Pulverizer overhaul | 23 | 23 | 1827.3 | 102290.1762
0346-Pulverizer pyrite removal system | 137 | 138 | 10970.28 | 69744.9519
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 89 | 89 | 10314.31 | 124338.8319
0358-Oil burner piping and valves | 5 | 5 | 1749.8 | 6437.5812
0359-Gas burner piping and valves | 138 | 139 | 23976.04 | 424894.001
0360-Burners | 165 | 165 | 14777.2 | 475903.8905
0361-Burner orfices | 1 | 1 | 240 | 9492
0370-Burner instruments and controls (except light-off) | 147 | 150 | 16378.49 | 118624.3098
0380-Light-off (igniter) systems (including fuel supply) | 80 | 80 | 14799.05 | 188545.8568
0385-Igniters | 98 | 100 | 17819.84 | 145512.9363
0390-Burner wind boxes and dampers | 17 | 17 | 2192 | 17110.8492
0400-Burner wind box fires | 7 | 7 | 1521.37 | 115868.8964
0410-Other burner problems | 113 | 117 | 5000.22 | 238986.9914
0415-Cyclone feeders | 151 | 151 | 10307.83 | 150238.2026
0420-Cyclone crusher | 19 | 19 | 1069 | 32150.5996
0425-Cyclone dampers | 18 | 18 | 2592.31 | 26239.0717
0426-Cyclone air ducts | 11 | 11 | 615 | 13058.3332
0430-Cyclone furnace | 12 | 12 | 473.57 | 30411.3957
0435-Other cyclone problems | 276 | 302 | 9707.07 | 56051.3439
0440-Fuel oil pumps (general) | 3 | 3 | 810 | 37643.2495
0441-Fuel oil pumps (burner supply) | 12 | 12 | 1269.32 | 6314.177
0442-Fuel oil pumps (forwarding/transfer) | 3 | 3 | 211 | 1411.2332
0443-Fuel oil (burner supply) pump drives | 1 | 1 | 33 | 60.5
0444-Fuel oil (forwarding/transfer) pump drives | 1 | 1 | 800 | 2200
0450-Fuel oil heaters | 2 | 2 | 237.9 | 983.3199
0460-Fuel oil atomizers | 4 | 4 | 737 | 6370.5996
0470-Oil and gas fires | 3 | 3 | 425.4 | 5553.16
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 83 | 83 | 9675.31 | 78585.4497
0500-Main steam piping up to turbine stop valves | 77 | 77 | 8102.09 | 437380.5679
0510-Main steam relief/safety valves off superheater | 57 | 57 | 8930.88 | 719568.9545
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 26 | 26 | 5733.85 | 364355.9339
0530-Other main steam system problems | 69 | 82 | 6982.1 | 284800.9072
0540-Hot reheat steam piping up to turbine stop valves | 25 | 25 | 5698.01 | 319546.9068
0541-Cold reheat steam piping up to boiler | 20 | 20 | 3671.1 | 163642.9321
0550-Reheat steam relief/safety valves | 21 | 21 | 3126 | 109155.1323
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 31 | 31 | 7775.09 | 43751.831
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 20 | 20 | 4517.7 | 75548.4248
0570-Other reheat steam problems | 66 | 67 | 9169.06 | 502217.4967
0580-Desuperheater/attemperator piping | 13 | 13 | 3934.74 | 123573.3945
0590-Desuperheater/attemperator valves | 53 | 53 | 11969.82 | 309218.9052
0600-Desuperheater/attemperator spray nozzles | 3 | 3 | 814 | 10430.9998
0620-Other desuperheater/attemperator problems | 13 | 13 | 1072.02 | 27933.93
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 4 | 4 | 934 | 2313.4498
0640-Startup bypass system valves | 37 | 37 | 16867 | 842227.5954
0650-Startup bypass tanks or flash tanks | 3 | 3 | 18 | 17097.6
0655-Steam by-pass system instrumentation and controls | 2 | 2 | 687 | 27507.1999
0660-Other startup bypass system problems | 3 | 3 | 870 | 67564.0664
0670-Feedwater piping downstream of feedwater regulating valve | 11 | 11 | 1752.3 | 93162.5492
0680-Feedwater valves (not feedwater regulating valve) | 59 | 59 | 12654.92 | 296541.2953
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 18 | 18 | 2292.1 | 16638.1613
0700-Blowdown system valves A | 3 | 3 | 483.3 | 7770.2431
0710-Blowdown system piping B | 27 | 27 | 5020.3 | 79123.2222
0720-Blowdown system controls / instrumentation | 1 | 1 | 287.87 | 2034.2811
0730-Other blowdown system problems | 6 | 6 | 2880.89 | 71621.8344
0740-Boiler recirculation pumps | 50 | 50 | 11737.1 | 519450.8059
0741-Boiler recirculation pumps - motors | 31 | 31 | 5064.5 | 351128.3017
0742-Boiler recirculation pumps - motors - cooling system | 4 | 4 | 2046 | 18149.8494
0750-Boiler recirculation piping including downcomers | 2 | 2 | 432.3 | 929484.5166
0760-Boiler recirculation valves | 13 | 13 | 5539 | 52280.0645
0770-Other boiler recirculation problems | 22 | 22 | 2673.7 | 16211.5823
0775-Economizer piping | 31 | 31 | 4052.67 | 223726.2972
0780-Headers between tube bundles | 4 | 4 | 457.3 | 111827.1666
0782-Headers and caps | 4 | 4 | 1291.48 | 24656.3736
0790-Pipe hangers; brackets; supports (general) | 1 | 1 | 110 | 4702.5
0799-Other miscellaneous piping system problems | 26 | 26 | 4756.82 | 155993.8255
0800-Drums and drum internals (single drum only) | 52 | 52 | 15539.51 | 158239.7554
0801-HP Drum (including drum level trips not attributable to other causes) | 70 | 70 | 11837.81 | 119569.243
0802-IP Drum (including drum level trips not attributable to other causes) | 36 | 38 | 7402.28 | 86674.2637
0803-LP Drum (including drum level trips not attributable to other causes) | 19 | 19 | 2340.72 | 14815.9776
0810-Boiler supports and structures (use code 1320 for tube supports) | 3 | 3 | 1157.53 | 109538.407
0820-Casing | 40 | 40 | 7006.09 | 1011662.3937
0830-Doors | 23 | 23 | 4956.96 | 216846.3491
0840-Refractory and insulation | 10 | 10 | 1634.5 | 119331.3163
0847-Other expansion joints | 5 | 5 | 484 | 55704.4664
0850-Other internal or structural problems | 15 | 15 | 1279.67 | 115598.1757
0855-Drum relief/safety valves (Single drum only) | 37 | 37 | 3672.03 | 202722.3537
0856-HP Drum relief/safety valves | 2 | 2 | 61 | 8723
0858-LP Drum relief/safety valves | 2 | 2 | 559.5 | 19035.1749
0859-Tube external fins/membranes A | 11 | 11 | 2293.85 | 202502.7767
0860-Soot blowers - air (see code 3844 for air delivery system) | 11 | 11 | 553.9 | 1184.8999
0870-Soot blowers - steam | 32 | 32 | 4825.88 | 124261.6293
0872-Soot blowers - water | 2 | 2 | 134 | 3042.1
0873-Soot blower drives | 1 | 1 | 180 | 6039
0876-Soot blower controls | 17 | 17 | 1364 | 13507.0494
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 54 | 54 | 6314.48 | 100707.0013
0885-Fly ash Removal System - wet transport | 1 | 1 | 85 | 2585.4166
0890-Bottom ash systems (wet or dry) | 140 | 140 | 14175.88 | 1020468.8656
0891-Bottom ash hoppers (including gates) | 62 | 62 | 11122.03 | 261818.8899
0892-Bottom ash clinker grinders | 10 | 10 | 2518 | 60098.1326
0893-Bottom ash water pumps and motors | 1 | 1 | 150 | 294.9999
0894-Bottom ash piping and valves | 12 | 12 | 3049 | 37774.8492
0895-Ashpit trouble | 5 | 5 | 742 | 7342.2665
0896-Bottom ash dewatering bin system; instruments and controls | 1 | 1 | 230 | 394.8332
0897-Bottom ash rotary (drag chain type) conveyor and motor | 113 | 113 | 27978.65 | 744337.573
0898-Bottom ash pyrite hopper (pulverizer reject) system | 2 | 2 | 693.04 | 3497.8132
0899-Bottom ash controls and instrumentation | 10 | 10 | 2328.42 | 34557.0549
0900-Slag-tap (cyclone furnace) | 22 | 22 | 3061.24 | 275481.248
0910-Slag-tap (other than cyclone furnace) | 1 | 1 | 364 | 65331.9332
0920-Other slag and ash removal problems A | 181 | 183 | 22881.64 | 744325.9953
0930-Bed material coolers | 1 | 1 | 95 | 251.75
0933-Bed material fans/blowers | 1 | 1 | 3.3 | 6.6
0950-Other bed material system problems | 3 | 3 | 483 | 70472.3664
0970-Flue gas-solids separator | 1 | 1 | 40 | 320
0989-Other bed solids recirculation problems | 7 | 7 | 106.1 | 2837.65
0991-Tube leaks | 17 | 17 | 1021.69 | 153766.7165
0999-Other heat exchanger problems | 5 | 5 | 6 | 23.8667
1000-Waterwall (Furnace wall) | 685 | 685 | 221635.02 | 19975916.4922
1003-Steam generating tubes between steam drum and mud drum | 30 | 30 | 3405.1 | 323513.5704
1005-Generating tubes | 30 | 30 | 3093.56 | 175082.5317
1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | 2 | 2 | 163.4 | 10465.7332
1010-Cyclone furnace (in cyclone area only) | 32 | 32 | 6457.24 | 602651.9099
1020-Convection pass wall (water tubes only) | 16 | 16 | 7620 | 407738.3314
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 13 | 13 | 6087 | 719178.8659
1035-Platen superheater | 33 | 33 | 14611.3 | 1389749.0769
1040-First superheater | 111 | 111 | 34374.81 | 3458856.5855
1050-Second superheater | 196 | 196 | 64747.55 | 5853160.4733
1055-External superheater link tubing | 4 | 4 | 2298 | 170036.9661
1060-First reheater | 160 | 160 | 62883.06 | 5037082.9607
1070-Second reheater | 40 | 40 | 21094 | 1476266.5257
1075-External reheater link tubing | 1 | 1 | 492.5 | 22499.0415
1080-Economizer | 113 | 114 | 24961.66 | 2416085.9995
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 14 | 14 | 3305 | 189873.9161
1090-Other boiler tube leaks | 123 | 123 | 30288.72 | 4117244.7371
1100-Waterwall (Furnace wall) | 75 | 81 | 19311.22 | 745640.252
1103-Steam generating tubes between steam drum and mud drum | 3 | 3 | 401.62 | 2639.68
1105-Generating tubes | 8 | 8 | 98.75 | 28101.9391
1110-Cyclone furnace (in cyclone area only) | 2 | 2 | 30 | 639.1667
1120-Convection pass wall | 8 | 9 | 962.74 | 82128.61
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 17 | 17 | 2867.94 | 277064.5426
1140-First superheater | 77 | 77 | 3970.3 | 229278.6673
1150-Second superheater | 125 | 126 | 36709.73 | 791605.8844
1160-First reheater | 100 | 104 | 12212.94 | 556047.6816
1170-Second reheater | 24 | 27 | 525.63 | 60000.3745
1180-Economizer | 21 | 21 | 1744.55 | 147220.501
1190-Other tube slagging or fouling | 59 | 59 | 7067.32 | 236784.4123
1191-Bed agglomeration (FBC only) | 7 | 7 | 313.2 | 22113.9065
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 56 | 76 | 7717.2 | 98627.1156
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 3 | 3 | 423 | 7107.5832
1300-Water side fouling | 1 | 1 | 240 | 4803.9998
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 2 | 2 | 482 | 4834.6165
1320-Tube supports/attachments | 2 | 2 | 502 | 50963.1663
1330-Slag fall damage | 3 | 3 | 2470 | 340953.6664
1340-Tube modifications (including addition and removal of tubes) | 1 | 1 | 502 | 15587.1
1350-Other miscellaneous boiler tube problems | 29 | 29 | 3097.39 | 1456197.9521
1360-Boiler drains system | 26 | 26 | 6194.92 | 179196.3201
1400-Forced draft fans | 229 | 229 | 19255.21 | 2681591.5964
1401-Forced draft fan dampers | 55 | 55 | 9900.01 | 286838.4373
1407-Forced draft fan lubrication system | 23 | 23 | 4501.68 | 215987.9879
1410-Forced draft fan motors | 98 | 98 | 20599.56 | 1832362.0914
1411-Forced draft fan motors - variable speed | 8 | 8 | 2772 | 23084.5163
1412-Forced draft fan drives (other than motor) | 41 | 41 | 7587.79 | 149498.9669
1413-Forced draft fan couplings | 12 | 12 | 1129.9 | 160641.343
1415-Forced draft fan controls | 59 | 59 | 8598.4 | 59712.964
1420-Other forced draft fan problems | 151 | 151 | 18216.77 | 666761.9292
1421-Secondary air fans/blowers | 15 | 15 | 1066.03 | 5217.9694
1422-Secondary air fan/blower motors - single speed | 4 | 4 | 413.4 | 23558.3399
1424-Secondary air fan/blower controls | 6 | 6 | 1352 | 6161.7331
1430-Air supply ducts from FD fan | 18 | 18 | 1425.34 | 167223.0348
1431-Air supply dampers from FD fan | 39 | 39 | 571 | 18270.3331
1432-Air supply duct expansion joints | 16 | 16 | 3434.16 | 145147.9895
1440-Air supply dampers | 16 | 16 | 1919.4 | 69955.1795
1450-Other air supply problems | 152 | 152 | 10807.2 | 243456.7161
1455-Induced draft fans | 677 | 679 | 55974.02 | 3986815.343
1456-Induced draft fan dampers | 127 | 127 | 13490.38 | 331097.0543
1457-Induced draft fan lubrication systems | 59 | 59 | 13131.17 | 202694.8333
1460-Induced draft fan fouling | 14 | 14 | 1058.2 | 40166.4063
1470-Induced draft fan motors and drives | 263 | 263 | 27258.74 | 2082240.265
1471-Induced draft fan motors - variable speed | 91 | 91 | 21710.48 | 194702.5023
1472-Inducted draft fan coupling | 8 | 8 | 641.53 | 51306.9055
1475-Induced draft fan controls | 125 | 125 | 24078.66 | 359154.4404
1476-Induced draft fan speed changer | 7 | 7 | 1660.64 | 12605.9889
1480-Other induced draft fan problems | 319 | 319 | 35852.79 | 1012650.3328
1487-Air heater (tubular) | 10 | 10 | 999 | 34633.483
1488-Air heater (regenerative) | 164 | 212 | 37003.44 | 3404564.4625
1489-Air heater (heat pipe; plate-type) | 11 | 11 | 830 | 188640.0329
1492-Air heater fouling (tubular) | 7 | 7 | 232.4 | 33992.2133
1493-Air heater fouling (regenerative) | 266 | 271 | 15745.01 | 823030.7583
1495-Other air heater fouling (heat pipe; plate-type) | 19 | 19 | 454.63 | 70620.1789
1500-Air heater soot blowers | 4 | 4 | 1013 | 18546.9
1510-Flue gas ducts (except recirculation) | 45 | 47 | 6751.4 | 2711093.7612
1512-Flue gas expansion joints | 13 | 13 | 1270.13 | 560482.6578
1520-Flue gas dampers (except recirculation) | 9 | 9 | 765.98 | 24330.8508
1530-Other flue gas problems | 97 | 97 | 5942.61 | 519131.4028
1535-Flue gas recirculating fan | 4 | 4 | 422 | 13634.1664
1550-Flue gas recirculation fan motors | 3 | 3 | 1288 | 7123.3994
1560-Other flue gas recirculation fan problems | 2 | 2 | 191 | 14970.8166
1570-Flue gas recirculation ducts | 1 | 1 | 347 | 5846.95
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 1 | 1 | 209 | 264071.5
1591-Stack damper and linkage | 4 | 4 | 963 | 5923.2329
1592-Stack damper linkage motors | 1 | 1 | 117 | 109.2
1599-Other miscellaneous boiler air and gas system problems | 239 | 239 | 16593.85 | 758206.2463
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 203 | 204 | 53168.35 | 443768.3985
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 125 | 126 | 24445.76 | 364250.4145
1720-Desuperheater/attemperator controls | 46 | 46 | 7675.96 | 143008.8953
1730-Boiler explosion or implosion | 22 | 22 | 677.87 | 24248.3154
1740-Boiler drum gage glasses/level indicator | 71 | 71 | 13242.41 | 99894.715
1741-Furnace and water gauge television auxiliary system | 1 | 1 | 63.77 | 139.2311
1750-Burner management system | 162 | 162 | 32896.21 | 329207.1973
1760-Feedwater instrumentation (not local controls) | 59 | 59 | 10081.86 | 73541.3723
1761-Combustion /Steam condition instrumentation (not local controls) | 20 | 20 | 4371.62 | 33915.9677
1762-Desuperheater/attemperator instrumentation (not local controls) | 13 | 13 | 2268.37 | 38860.9532
1799-Other boiler instrumentation and control problems | 235 | 235 | 48239.66 | 1020467.1648
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 1 | 1 | 198 | 1022.9999
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 47 | 47 | 4638.9 | 133593.814
1810-Other boiler inspections | 1 | 1 | 54 | 162
1811-Boiler Inspections - problem identification/investigative | 1 | 1 | 20 | 850
1812-Boiler Inspections - scheduled or routine | 12 | 12 | 540.2 | 20590.2216
1820-Chemical cleaning/steam blows | 1 | 1 | 51.5 | 978.5
1850-Boiler water condition (not feedwater water quality) | 380 | 380 | 53948.56 | 790117.3295
1900-Improper balance between tube sections not due to fouling or plugging | 1 | 1 | 145 | 14.5
1910-Inadequate air not due to equipment problems | 129 | 129 | 1279.6 | 186890.8169
1980-Boiler safety valve test | 14 | 14 | 1301.88 | 6916.5636
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 25 | 25 | 3579 | 113035.3987
1999-Boiler; miscellaneous | 905 | 1186 | 32593.78 | 1490488.068
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 7 | 7 | 611.22 | 32620.358
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 23 | 24 | 3133.86 | 64415.4794
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 11 | 11 | 1072.74 | 24622.7595
2033-Fuel limits - MAPLHGR (Maximum Average Planar Linear Heat Generation Rate - BWR units only) | 1 | 1 | 1 | 6228
2061-Incore nuclear instrumentation | 2 | 2 | 1699.78 | 577934.0781
2070-Normal refueling | 1 | 1 | 987 | 87431.7497
2112-Control rod hydraulic drives | 2 | 2 | 282.13 | 334.1315
2151-Control rod drive controls | 2 | 2 | 2142.42 | 132465.8198
2155-Control rod testing | 1 | 1 | 15 | 60
2160-Other control rod drive problems | 13 | 13 | 5666 | 322105.9652
2170-Reactor vessel flanges and seals | 1 | 1 | 76 | 40.5333
2172-Feedwater sparges | 1 | 1 | 22 | 3356.1
2199-Other reactor vessel problems | 1 | 1 | 768.88 | 235443.8702
2200-Reactor coolant/recirculating pumps | 16 | 16 | 9512.94 | 395680.3127
2210-Reactor coolant/recirculating pump motors | 5 | 5 | 3006.16 | 335933.6406
2220-Reactor coolant/recirculating pump MG sets | 8 | 8 | 4372.89 | 268582.0372
2330-Pressurizer level instruments and controls | 1 | 1 | 20 | 560
2350-BWR feedwater controls | 5 | 5 | 1216.83 | 53364.985
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 15 | 15 | 8372 | 46530.5963
2380-Reactor control system/integrated control system problems | 4 | 4 | 503 | 54981.6667
2390-Other reactor coolant system instruments and controls | 6 | 6 | 3025.96 | 123018.2197
2399-Other miscellaneous reactor coolant system problems | 7 | 7 | 3798.43 | 186894.644
2440-Steam generator chemistry (excluding feedwater chemistry) | 7 | 7 | 88.78 | 14059.6065
2460-Blowdown system valves B | 1 | 1 | 2.52 | 1874.88
2480-Other blowdown | 1 | 1 | 1 | 2.0667
2500-Steam piping (up to turbine stop valves and bypass valves) | 4 | 4 | 2650.3 | 455695.8257
2510-Main steam isolation valves (BWR and PWR) | 6 | 6 | 3445.19 | 313360.2571
2520-Main steam safety/relief valves (except BWR) | 3 | 3 | 1971.37 | 146813.8969
2521-Main steam safety/relief valve testing | 1 | 1 | 4 | 66.6667
2530-Atmospheric or condenser dump valves (not SRVs) | 7 | 10 | 579.4 | 90154.7079
2540-Other steam valves | 2 | 2 | 839 | 51077.1333
2599-Other steam generator problems | 1 | 1 | 49 | 5927.3666
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 3 | 3 | 2606.8 | 349014.2892
2602-Steam turbine drives for high pressure pumps (including RCIC) | 1 | 1 | 4.5 | 5.025
2624-Low pressure heat exchangers | 1 | 1 | 95 | 6958.75
2649-Other emergency core cooling/residual heat removal system problems | 3 | 3 | 1800 | 91557.8329
2660-Safeguard buses and associated equipment (transformers; breakers; etc.) | 1 | 1 | 10 | 35
2720-Containment isolation valves and dampers | 1 | 1 | 768.88 | 97955.312
2770-Containment cooling system - normal | 4 | 4 | 1775.93 | 302878.7112
2816-Valves and piping | 1 | 1 | 292.86 | 541.791
2817-Instruments and controls | 1 | 1 | 13.4 | 43.55
2840-Auxiliary feedwater pumps | 1 | 1 | 14.8 | 33.5467
2999-Other miscellaneous nuclear reactor problems | 5 | 5 | 146 | 716.4666
3110-Condenser tube leaks | 195 | 195 | 44249.34 | 2148744.7428
3111-Condenser tube fouling shell side | 22 | 22 | 1323 | 23381.4661
3112-Condenser tube fouling tube side | 217 | 218 | 9716.75 | 793101.9151
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 232 | 235 | 27612.55 | 192182.7634
3114-Air-cooled condenser tubes | 3 | 3 | 51 | 397.3333
3115-Air-cooled condenser pumps | 2 | 2 | 153 | 16534.7499
3116-Air-cooled condenser fans | 6 | 6 | 229 | 8538.0332
3117-Air-cooled condenser fan motors | 2 | 2 | 85.28 | 83.6693
3118-Other Air-cooled condenser problems | 38 | 38 | 2620.59 | 16384.1866
3119-Other condenser tube casing or shell and internal problems | 7 | 7 | 1080.21 | 60383.7365
3120-Tube sheets | 9 | 9 | 3463.69 | 211134.5893
3121-Expansion joint | 12 | 12 | 4548.3 | 765940.2541
3122-Gaskets and seals | 6 | 6 | 1821.4 | 4444.4527
3123-Hot well | 13 | 13 | 3630.7 | 139669.8654
3124-Tube sheet fouling | 39 | 39 | 1519.06 | 29300.7686
3129-Other condenser casing or shell and internal problems | 11 | 11 | 1794 | 172210.5161
3130-Air ejectors | 29 | 29 | 1015.7 | 39686.558
3131-Air ejector piping and valves | 10 | 10 | 1644.66 | 84247.8304
3132-Inter and after condensers | 3 | 3 | 98 | 1165.4
3133-Vacuum pumps | 29 | 29 | 5922.63 | 44171.0506
3134-Vacuum pump piping and valves | 4 | 4 | 137.03 | 1148.4669
3135-Vacuum pump motor and auxiliaries | 2 | 2 | 530 | 5362.8331
3139-Other air extraction system problems - general | 11 | 11 | 1672.8 | 22969.9458
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 352 | 352 | 31495.99 | 767261.3037
3150-Hot well level controls | 26 | 26 | 4557.55 | 46735.2491
3151-Vacuum pump and air ejector controls | 9 | 9 | 1379 | 9334.9827
3152-Air-cooled condenser controls | 3 | 3 | 550 | 14667.8333
3159-Other condensing system controls and instruments | 21 | 21 | 1924.9 | 115524.6526
3186-Auxiliary Condenser and Associated Equipment | 41 | 41 | 6941.24 | 81069.3091
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 38 | 38 | 4589.12 | 141638.8524
3199-Other miscellaneous condensing system problems | 59 | 60 | 8971.96 | 1341588.0825
3210-Circulating water pumps | 192 | 192 | 26708.46 | 1697803.3957
3211-Circulating water pump motors | 148 | 148 | 18956.56 | 1231923.2484
3220-Circulating water piping | 45 | 45 | 12324.24 | 774332.8248
3221-Circulating water piping fouling | 9 | 9 | 739.8 | 16811.6897
3230-Circulating water valves | 32 | 32 | 5122.42 | 62944.7827
3231-Waterbox | 24 | 24 | 3105.6 | 26175.623
3232-Condenser tube cleaning system including debris filter | 12 | 12 | 1313 | 14994.3496
3233-Circulating water priming system | 3 | 3 | 278 | 9727.1166
3235-Cooling tower booster pump | 1 | 1 | 33.38 | 90.126
3238-Cooling tower fan motors | 14 | 14 | 1383 | 12204.5161
3239-Cooling tower fan motors - variable speed | 1 | 1 | 116 | 2298.7333
3240-Cooling tower fans | 57 | 57 | 3788.67 | 77583.9843
3241-Cooling tower efficiency below design | 10 | 10 | 361 | 3304.9999
3242-Cooling tower fill damage | 1 | 1 | 446 | 16390.5
3243-Cooling tower icing | 8 | 8 | 908.4 | 36242.8098
3245-Other cooling tower problems | 83 | 86 | 10089.44 | 584599.5197
3246-Cooling tower fouling | 4 | 4 | 397.2 | 3146.9731
3247-Cooling tower instrumentation | 8 | 8 | 1533.5 | 79828.2408
3250-Circulating water system instruments and controls | 17 | 17 | 2981.5 | 15647.6908
3260-Traveling screens | 38 | 38 | 5915.95 | 385483.4918
3261-Traveling screen fouling | 18 | 18 | 3860.32 | 26283.1057
3269-Circulating water biological conditions (ie; zebra mussels) | 31 | 31 | 4795.35 | 75374.5048
3270-Intake system problems other than traveling screens | 16 | 16 | 3396.2 | 42588.9271
3271-Intake grating fouling | 32 | 32 | 4488.99 | 50255.1938
3272-Circulating water screenwash system | 15 | 15 | 1550.84 | 20621.8429
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 60 | 62 | 7913.57 | 59425.1732
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 17 | 17 | 3097.55 | 75063.3158
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 76 | 76 | 2177.94 | 222747.8351
3281-Circulating water tempering system | 7 | 7 | 242 | 2140.7166
3282-Circulating water cooling ponds | 2 | 2 | 50 | 1488.8333
3285-Circulating water chemistry | 15 | 15 | 3590.6 | 300225.7773
3290-Waste water (zero discharge) tanks; pumps and motors | 1 | 1 | 228.73 | 55844.4295
3292-Waste water (zero discharge) piping | 4 | 4 | 1130 | 1001.1663
3299-Other circulating water system problems | 44 | 44 | 5833 | 165570.0803
3300-Condensate water pre-treatment | 26 | 26 | 5425.5 | 95795.1151
3310-Condensate/hotwell pumps | 128 | 128 | 23733.64 | 1196264.1151
3311-Condensate/hotwell pump motor | 41 | 41 | 7626.61 | 239230.759
3312-Condensate booster pump | 18 | 18 | 2998.4 | 87195.7906
3313-Condensate booster pump motor | 8 | 8 | 869.18 | 122233.4919
3314-Condensate booster pump motor - variable speed | 2 | 2 | 336.69 | 611.4033
3315-Condensate booster pump drive (other than 3313 and 3314) | 1 | 1 | 255 | 1521.4998
3320-Condensate piping | 28 | 28 | 6375.51 | 179913.3775
3330-Condensate valves | 38 | 38 | 6699.95 | 73689.4229
3340-LP heater tube leaks | 14 | 14 | 1752.82 | 288925.385
3341-Other LP heater - general | 15 | 16 | 1659.77 | 7781.0202
3342-IP heater tube leaks | 7 | 7 | 559 | 58345.5664
3343-Other IP heater - general | 4 | 4 | 338 | 7827.3332
3344-Deaerator (including level control) | 88 | 88 | 15890.75 | 270201.3759
3345-IP heater head leaks | 33 | 43 | 1399 | 52362.0662
3350-Condensate polishing and filtering systems | 33 | 33 | 5470.28 | 104694.8905
3351-Chemical addition systems | 1 | 1 | 109 | 89.0166
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 115 | 115 | 21611.42 | 562050.0215
3360-Condensate makeup and return (including storage tanks) | 25 | 25 | 4678.1 | 188416.3436
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 25 | 25 | 4227.7 | 113096.6361
3380-Condensate coolers | 2 | 2 | 583 | 1609.3
3399-Other miscellaneous condensate system problems | 35 | 35 | 5444.72 | 106851.8173
3401-Startup feedwater pump | 29 | 29 | 10444.55 | 420017.7019
3407-Feedwater pump suction screens | 13 | 13 | 3425.29 | 48607.425
3408-Feedwater pump drive - local controls | 73 | 73 | 19718.87 | 227796.1845
3409-Feedwater pump drive motor - variable speed | 8 | 8 | 645 | 24222.5831
3410-Feedwater pump | 386 | 386 | 76892.96 | 4713591.2341
3411-Feedwater pump drive - motor | 85 | 85 | 10499.21 | 1255426.5301
3412-Feedwater pump drive - steam turbine | 156 | 157 | 45639.57 | 1436661.334
3413-Feedwater pump coupling and drive shaft | 21 | 21 | 5031.7 | 199038.5147
3414-Feedwater pump local controls | 58 | 58 | 20989.38 | 134540.5595
3415-Feedwater pump/drive lube oil system | 99 | 99 | 21740.8 | 634878.2078
3416-Other feedwater pump problems | 130 | 130 | 26603.91 | 559318.0545
3418-Feedwater pump drive - other | 9 | 9 | 1984.91 | 50159.4213
3419-Feedwater pump drive - gear | 1 | 1 | 95 | 834.4166
3420-Feedwater piping and supports | 31 | 31 | 8891.72 | 899538.4522
3430-Feedwater regulating (boiler level control) valve | 145 | 145 | 32656.99 | 1031081.8567
3431-Other feedwater valves | 199 | 216 | 31792.23 | 658322.1806
3439-HP heater head leaks | 36 | 39 | 2721.2 | 173824.2661
3440-High pressure heater tube leaks | 118 | 118 | 16854.29 | 1496477.236
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 97 | 103 | 9345.71 | 645242.814
3451-Feedwater Booster Pump Suction Screens | 1 | 1 | 481 | 1771.6832
3454-Feedwater Booster Pump | 21 | 21 | 5335.26 | 153915.8674
3455-Feedwater Booster Pump Drive - Motor | 12 | 12 | 3599.4 | 96664.9553
3458-Feedwater Booster Pump Local Controls | 3 | 3 | 1132.2 | 2520.5732
3459-Feedwater Booster Pump/Drive Lube Oil System | 9 | 9 | 2253.04 | 21623.5764
3460-Other Feedwater Booster Pump Problems | 12 | 12 | 2769.3 | 158804.6641
3499-Other feedwater system problems | 132 | 132 | 24503.54 | 433690.8383
3501-Heater drain pumps | 29 | 29 | 2647.48 | 45276.9907
3502-Heater level control | 52 | 52 | 7562.4 | 129308.6002
3503-Heater drain piping | 11 | 11 | 2122 | 42054.4324
3504-Heater drain valves | 32 | 32 | 5932.9 | 258662.0387
3505-Heater drain pump drive | 7 | 7 | 481.25 | 6761.4164
3509-Other heater drain system problems | 6 | 6 | 902.24 | 13036.7237
3520-HP Extraction steam piping | 1 | 1 | 479 | 958
3521-HP Extraction steam valves | 101 | 157 | 6616.89 | 142573.0285
3522-HP Extraction steam instruments and controls | 3 | 3 | 182.5 | 175.6166
3529-Other HP extraction steam system problems | 5 | 5 | 720 | 5113.6495
3530-IP Extraction steam piping | 1 | 1 | 390.66 | 12813.648
3531-IP Extraction steam valves | 10 | 10 | 2476 | 133779.8842
3532-IP Extraction steam instruments and controls | 2 | 2 | 188 | 381
3539-Other IP extraction steam system problems | 4 | 4 | 458.4 | 12509.4398
3540-LP Extraction steam piping | 23 | 23 | 6669.7 | 392478.2567
3541-LP Extraction steam valves | 16 | 16 | 4388.49 | 174524.9869
3542-LP Extraction steam instruments and controls | 6 | 6 | 1112.54 | 88657.6661
3600-Switchyard transformers and associated cooling systems - external | 33 | 33 | 4905.16 | 772680.4889
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 17 | 17 | 1934.17 | 89121.5219
3610-Switchyard circuit breakers - (not outside management control) | 58 | 58 | 7252.75 | 187229.8479
3611-Switchyard circuit breakers - external | 112 | 112 | 16289.97 | 335428.9556
3612-Switchyard system protection devices - external | 101 | 101 | 12548.2 | 353104.957
3613-Switchyard system protection devices - (not outside management control) | 63 | 63 | 5038.26 | 46840.8649
3618-Other switchyard equipment ? (not outside management control) | 25 | 25 | 3114.44 | 112669.1003
3619-Other switchyard equipment - external | 153 | 153 | 18020.03 | 954123.6754
3620-Main transformer | 364 | 364 | 43280.98 | 10472810.8067
3621-Unit auxiliaries transformer | 130 | 130 | 28710.18 | 1266993.4144
3622-Station service startup transformer | 28 | 28 | 6924.98 | 929914.4316
3623-Auxiliary generators | 14 | 14 | 1821.89 | 66355.8789
3624-Generator Voltage Supply System | 21 | 21 | 3801.03 | 111274.012
3629-Other switchyard or high voltage system problems - external | 92 | 92 | 9056.76 | 934640.3427
3630-480-volt transformers | 23 | 23 | 3009.55 | 34280.4777
3631-480-volt circuit breakers | 84 | 84 | 14328.23 | 150844.3278
3632-480-volt conductors and buses | 12 | 12 | 1676.4 | 131746.9327
3634-480-volt protection devices | 13 | 13 | 1064.4 | 6848.3514
3639-Other 480-volt problems | 36 | 36 | 5515.97 | 445302.0322
3640-AC instrument power transformers | 6 | 6 | 1785.35 | 77415.2244
3641-AC Circuit breakers | 88 | 88 | 11801.01 | 134868.3608
3642-AC Conductors and buses | 17 | 17 | 2916.55 | 142282.1933
3643-AC Inverters | 14 | 14 | 4207.34 | 117219.3833
3644-AC Protection devices | 96 | 96 | 9986.8 | 257681.1578
3649-Other AC instrument power problems | 25 | 25 | 2210.96 | 16474.4779
3650-DC instrument power battery chargers | 21 | 21 | 2124.9 | 28983.3829
3651-DC circuit breakers | 11 | 11 | 1463.2 | 8563.0394
3652-DC conductors and buses | 7 | 7 | 769.93 | 39389.5983
3653-DC protection devices | 26 | 26 | 2650.53 | 43725.7355
3659-Other DC power problems | 49 | 49 | 4064.92 | 153171.8732
3660-4160-volt transformers | 10 | 10 | 2175 | 41337.7492
3661-4160-volt circuit breakers | 106 | 108 | 23888.35 | 512969.189
3662-4160-volt conductors and buses | 41 | 41 | 9221.75 | 424876.2224
3663-4160-volt insulators | 1 | 1 | 615 | 11387.7496
3664-4160-volt protection devices | 41 | 41 | 7295.13 | 58953.1109
3669-Other 4160-volt problems | 21 | 21 | 6264.36 | 162693.4682
3670-12kV transformers | 5 | 5 | 1032 | 189528.5997
3671-12kV circuit breakers | 31 | 31 | 3325.54 | 109833.5362
3672-12kV conductors and buses | 36 | 36 | 2454.62 | 668229.9374
3673-12kV insulators | 4 | 4 | 248.44 | 51813.5023
3674-12kV protection devices | 26 | 26 | 2009.43 | 45259.3871
3679-Other 12kV problems | 12 | 12 | 1323.01 | 62735.257
3680-Other voltage system transformers | 6 | 6 | 1449.7 | 169864.288
3681-Other voltage system breakers | 60 | 60 | 8165.53 | 574029.5686
3682-Other voltage system conductors and buses | 35 | 35 | 5835.53 | 126561.8099
3683-Other voltage system insulators | 8 | 8 | 825 | 54246.7466
3684-Other voltage system protection devices | 59 | 59 | 5879.95 | 103038.9207
3689-Other Other voltage system problems | 41 | 41 | 5999.98 | 348727.5486
3690-Station Service Power Distribution System; General | 65 | 66 | 6708.97 | 242863.5071
3700-Power Station switchyard (non generating unit equipment) | 47 | 47 | 3670.37 | 116140.8632
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 76 | 76 | 5741.44 | 323521.2194
3720-Transmission equipment at the 1st substation) | 60 | 60 | 9935.35 | 368277.1268
3730-Transmission equipment beyond the 1st substation | 54 | 54 | 5058.47 | 271765.369
3800-Open cooling water pumps and motors | 5 | 5 | 299.4 | 2159.3995
3801-Open cooling water piping | 5 | 5 | 558 | 4031.9998
3802-Open cooling water valves | 1 | 1 | 130 | 396.5
3804-Open cooling water system fouling | 3 | 3 | 1630 | 5632.4998
3805-Open cooling water system instrumentation | 10 | 10 | 1220 | 5548.3496
3806-Open cooling water strainer | 7 | 7 | 566 | 7896.3499
3809-Other open cooling water problems | 4 | 4 | 639 | 547.4831
3810-Service water pumps and motors | 10 | 10 | 1653.37 | 7359.336
3811-Service water piping | 47 | 47 | 5491.33 | 493504.7183
3812-Service water valves | 7 | 7 | 1396.17 | 36877.7044
3813-Service water heat exchangers | 6 | 6 | 359.32 | 32372.0067
3814-Service water system fouling | 8 | 8 | 234.08 | 3232.5979
3815-Service water strainer | 4 | 4 | 845 | 773.883
3819-Other service water problems A | 24 | 24 | 3820.35 | 96954.1952
3820-Closed cooling water pumps | 15 | 15 | 2742.41 | 44135.4608
3821-Closed cooling water piping | 12 | 12 | 2211.01 | 150560.3378
3822-Closed cooling water valves | 17 | 17 | 1505.89 | 23405.6842
3823-Closed cooling water heat exchangers | 17 | 18 | 2608 | 42889.8994
3824-Closed cooling water system fouling | 11 | 11 | 897.93 | 9976.9311
3825-Closed cooling water instrumentation | 2 | 2 | 364 | 4363.5832
3829-Other closed cooling water system problems A | 43 | 43 | 4213.84 | 33024.1822
3830-Auxiliary boiler | 32 | 32 | 10661.08 | 229171.9871
3831-Auxiliary steam piping | 14 | 14 | 1358.9 | 94170.1311
3832-Auxiliary steam valves | 40 | 40 | 9249.77 | 312176.278
3833-Auxiliary steam controls and instruments | 13 | 13 | 3525.7 | 66277.5779
3834-Auxiliary boiler tube leaks | 12 | 12 | 4284.9 | 223649.8155
3835-Auxiliary boiler burner management system | 5 | 5 | 2375.4 | 23583.084
3836-Steam Transfer to Other Unit | 110 | 130 | 5385.65 | 175840.013
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 24 | 24 | 3805 | 166228.5826
3840-Service air compressors | 40 | 40 | 4192.72 | 18268.66
3841-Service air piping | 3 | 3 | 54 | 435
3842-Service air valves | 4 | 4 | 877.74 | 7112.7642
3843-Service air dryers | 3 | 3 | 282 | 1052.7999
3844-Soot blowing air compressor and system | 4 | 4 | 1293.1 | 16163.0179
3849-Other service air problems | 3 | 3 | 826 | 48020.4166
3850-Instrument air compressors | 34 | 34 | 8905.39 | 62677.0292
3851-Instrument air piping | 24 | 24 | 4331.99 | 37217.7968
3852-Instrument air valves | 13 | 13 | 1261.46 | 16430.8213
3853-Instrument air dryers | 4 | 4 | 460.1 | 1566.4664
3859-Other instrument air problems | 21 | 21 | 3758.7 | 17349.7883
3860-Fire protection system pumps | 1 | 1 | 24.9 | 90.885
3861-Fire protection system piping | 15 | 15 | 1158.26 | 66948.2879
3862-Fire protection system valves | 8 | 8 | 542 | 13755.1498
3863-Fire protection system fouling | 1 | 1 | 800 | 49093.3328
3864-Fire protection system instrumentation and controls | 84 | 84 | 6778.96 | 98701.8376
3869-Other fire protection system problems | 59 | 59 | 3961.21 | 129827.2186
3870-Fuel Gas Compressor and Motors | 66 | 66 | 2864.36 | 220098.8606
3871-Fuel Gas Compressor Piping | 4 | 4 | 370.1 | 3380.5333
3872-Fuel Gas Compressor Valves | 47 | 47 | 4676.97 | 45764.0035
3873-Fuel Gas Compressor Heat Exchangers | 17 | 17 | 333.1 | 2242.5315
3874-Fuel Gas Compressor Controls and Instrumentation | 77 | 77 | 6194.17 | 87274.6069
3875-Fuel Gas Compressor Filters | 5 | 5 | 406.3 | 26227.7749
3876-Fuel Gas Compressor Fire System | 5 | 5 | 941.6 | 8335.5499
3879-Fuel Gas Compressor - other | 115 | 116 | 5932.56 | 55741.4273
3880-Seal air fan | 1 | 1 | 339 | 1271.25
3881-Seal air fan drive - motor | 1 | 1 | 28 | 17273.2
3889-Other seal air fan system problems | 1 | 1 | 770 | 58751
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 99 | 99 | 5923.17 | 107268.2467
3899-Other miscellaneous auxiliary system problems | 111 | 111 | 15824.55 | 263035.7419
3950-Process computer | 44 | 44 | 4968.19 | 37123.5418
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 217 | 221 | 4724.72 | 585157.2271
3970-Distributive Control System (DCS) - process computer | 115 | 128 | 14192.35 | 108341.7804
3971-DCS - data highway | 55 | 56 | 7777.6 | 47935.4312
3972-DCS - hardware problems (including card failure) | 148 | 149 | 26311.17 | 309868.7557
3973-DCS - internal and termination wiring | 28 | 28 | 4563.6 | 37031.8555
3974-DCS - logic problems | 96 | 97 | 16937.86 | 141985.6312
3975-DCS - upgrades | 6 | 9 | 145.9 | 1392.5933
3979-Other DCS problems | 92 | 92 | 15826.73 | 125879.8763
3980-Programmable Logic Controller (PLC) | 25 | 25 | 1783.11 | 6359.8368
3981-PLC - data highway | 8 | 8 | 596.9 | 3933.0766
3982-PLC - hardware problems (including card failure) | 51 | 51 | 5115.42 | 62148.096
3983-PLC - internal and termination wiring | 5 | 5 | 300 | 2021.5499
3984-PLC - logic problems | 19 | 19 | 1015.4 | 15450.8513
3985-PLC - upgrades | 15 | 15 | 675.9 | 1416.6447
3989-Other PLC problems | 31 | 31 | 2537.22 | 19071.9378
3995-Powerhouse heating and ventilating systems | 1 | 1 | 92.4 | 462
3996-Air conditioning systems - rooms and areas | 6 | 6 | 880.13 | 1561.8922
3998-Balance of plant overhaul/outage | 10 | 10 | 2044.68 | 153364.9525
3999-Other miscellaneous balance of plant problems | 552 | 589 | 52786.65 | 2846101.2226
4000-Outer casing A | 6 | 6 | 2376.07 | 56678.3367
4001-Inner casing C | 3 | 3 | 1451 | 7125.3159
4010-Nozzles and nozzle blocks C | 2 | 2 | 295.3 | 53870.0282
4011-Diaphragms A | 6 | 6 | 536 | 237321.4166
4012-Buckets or blades A | 6 | 6 | 2794 | 1662016.0653
4014-Bucket or blade fouling C | 18 | 18 | 347 | 166456.9999
4015-Wheels or spindles A | 1 | 1 | 457 | 4029.2164
4020-Shaft seals B | 4 | 4 | 527 | 16617.9165
4030-Rotor shaft C | 6 | 6 | 2563 | 827105.3662
4040-Bearings C | 78 | 79 | 16000.86 | 1742498.0727
4041-HP steam turbine thrust bearings | 27 | 27 | 3783.54 | 85711.4557
4099-Other high pressure turbine problems | 71 | 71 | 7885.34 | 396089.6613
4100-Outer casing B | 2 | 2 | 346 | 17481.4332
4111-Diaphragms B | 1 | 1 | 225 | 261022.5
4112-Buckets or blades B | 8 | 8 | 1099 | 2528893.4496
4113-Bucket or blade fouling B | 38 | 38 | 468 | 81971.3332
4130-Rotor shaft B | 8 | 8 | 4120 | 1639608.116
4140-Bearings D | 14 | 14 | 3573 | 112455.0825
4199-Other intermediate pressure turbine problems | 25 | 27 | 9766.15 | 112768.2725
4201-Inner casing A | 2 | 2 | 635 | 28516.3333
4211-Diaphragms C | 2 | 2 | 340 | 3597
4212-Buckets or blades C | 13 | 13 | 1750 | 2410450.1833
4220-Shaft seals D | 4 | 4 | 353.5 | 7387.4666
4230-Rotor shaft A | 3 | 3 | 1260 | 1800745.8331
4240-Bearings E | 16 | 16 | 4180.3 | 377465.4657
4241-LP steam turbine thrust bearings | 3 | 3 | 124 | 15859.5499
4250-Other low pressure turbine problems | 76 | 77 | 14479.99 | 204066.4514
4260-Main stop valves | 144 | 154 | 31198.82 | 1111134.4459
4261-Control valves | 282 | 282 | 58753.94 | 2529332.2496
4262-Intercept valves | 52 | 52 | 14199.11 | 222659.4191
4263-Reheat stop valves | 39 | 39 | 10698.52 | 143200.8349
4264-Combined intercept valves | 6 | 6 | 1007.06 | 2767.2631
4265-Miscellaneous drain and vent valves | 37 | 37 | 7129.78 | 112233.7322
4266-Main stop valve testing | 7 | 7 | 1078 | 2570.7996
4267-Control valve testing | 39 | 42 | 6180.66 | 45808.331
4268-Reheat/intercept valve testing | 4 | 4 | 1127 | 10996.2331
4269-Other turbine valves (including LP steam admission valves) | 79 | 79 | 16585.39 | 803786.0758
4270-Crossover or under piping | 24 | 25 | 6573.63 | 346667.8234
4279-Miscellaneous turbine piping | 40 | 40 | 12370.47 | 468640.53
4280-Lube oil pumps A | 27 | 27 | 4938.63 | 372706.2374
4281-Lube oil coolers A | 15 | 15 | 3990.04 | 185945.1134
4283-Lube oil system valves and piping | 28 | 28 | 6156.77 | 78460.9606
4284-Lube oil pump drive | 14 | 14 | 3827 | 660284.1606
4289-Other lube oil system problems | 72 | 72 | 12435.1 | 567396.8672
4290-Hydraulic system pumps | 20 | 20 | 5617 | 41180.7483
4291-Hydraulic system coolers | 2 | 2 | 579.15 | 2735.8275
4292-Hydraulic system filters | 5 | 5 | 1326 | 18487.0329
4293-Hydraulic system pipes and valves | 86 | 86 | 21911.98 | 547222.6421
4299-Other hydraulic system problems | 61 | 61 | 13548.52 | 261409.3714
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 37 | 37 | 9886.51 | 85661.62
4301-Turbine governing system | 65 | 65 | 9728.03 | 171956.5548
4302-Turbine trip devices (including instruments) | 149 | 150 | 33254.18 | 471642.8417
4303-Exhaust hood and spray controls | 16 | 18 | 3678.66 | 15138.9393
4304-Automatic turbine control systems - mechanical | 8 | 8 | 1997.56 | 11495.3763
4305-Automatic turbine control systems - mechanical - hydraulic | 15 | 15 | 3700.7 | 26894.5628
4306-Automatic turbine control systems - electro-hydraulic - analog | 15 | 16 | 5893 | 361160.7085
4307-Automatic turbine control systems - electro-hydraulic - digital | 15 | 15 | 4666.36 | 86368.5772
4308-Automatic turbine control systems - digital control and monitoring | 47 | 47 | 10259.77 | 82836.572
4309-Other turbine instrument and control problems | 103 | 104 | 20027.69 | 280679.0428
4310-Steam Turbine Control System - data highway | 15 | 15 | 4795.3 | 88267.2586
4311-Steam Turbine Control System - hardware problems (including card failure) | 65 | 65 | 15210.85 | 132387.7595
4312-Steam Turbine Control System - internal and termination wiring | 7 | 7 | 867.7 | 9628.5548
4313-Steam Turbine Control System - logic problems | 86 | 86 | 16137.35 | 132451.5143
4314-Steam Turbine Control System - upgrades | 2 | 2 | 140.1 | 729.92
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 5 | 5 | 973.78 | 529510.059
4401-Inspection F | 1 | 1 | 17.85 | 1688.9075
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 688 | 76201.5665
4410-Turning gear and motor A | 47 | 47 | 11018.62 | 328497.8555
4411-Steam turbine gear box (single shaft configuration) | 1 | 1 | 20 | 175200
4412-Steam turbine clutch (single shaft configuration) | 1 | 1 | 25 | 265.4167
4415-Shaft coupling mechanism | 4 | 4 | 634.27 | 177637.7015
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 244 | 249 | 46221.8 | 5856459.3666
4430-Gland seal system | 69 | 69 | 12742.66 | 135285.253
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 9 | 9 | 4032.34 | 494577.9833
4445-Steam reheater | 3 | 3 | 18.1 | 5663.8853
4450-Water induction | 5 | 5 | 1596 | 10615.8324
4460-Turbine overspeed trip test | 11 | 13 | 3450 | 4990.4324
4470-Differential expansion | 72 | 72 | 19530.89 | 1649842.9055
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 22 | 22 | 4012.8 | 177246.3256
4499-Other miscellaneous steam turbine problems | 307 | 307 | 49064.92 | 1591859.1618
4500-Rotor windings (including damper windings and fan blades on hydro units) | 20 | 20 | 2446.18 | 1964065.1483
4510-Rotor collector rings | 19 | 19 | 3234.42 | 2384077.5943
4511-Rotor; General | 29 | 29 | 3334.88 | 2083641.2947
4520-Stator windings; bushings; and terminals | 53 | 53 | 4273.82 | 5151255.6871
4530-Stator core iron | 2 | 2 | 147 | 1281.8166
4535-Stator; General | 71 | 71 | 15610.6 | 1709336.8583
4536-Generator heaters | 1 | 1 | 20 | 1227
4540-Brushes and brush rigging | 25 | 25 | 4058.02 | 218676.3757
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 142 | 142 | 10850.18 | 1533415.9654
4551-Generator bearings | 102 | 103 | 18379.91 | 2562321.6818
4552-Generator lube oil system | 123 | 126 | 10000.01 | 326294.7406
4555-Bearing cooling system A | 33 | 33 | 2154.3 | 49547.0201
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 139 | 139 | 17353.83 | 1058812.8123
4570-Generator casing | 5 | 5 | 1468 | 92860.1995
4580-Generator end bells and bolting | 5 | 5 | 613 | 64502.0332
4590-Generator brakes | 48 | 48 | 4989.67 | 42659.085
4600-Exciter drive - motor | 16 | 16 | 2175.15 | 21420.3823
4601-Exciter field rheostat | 17 | 17 | 2096.75 | 335633.7721
4602-Exciter commutator and brushes | 37 | 37 | 4037.54 | 740288.7565
4603-Solid state exciter element | 49 | 50 | 5898.14 | 358244.1523
4604-Exciter drive - shaft | 13 | 13 | 619.2 | 113251.2065
4605-Exciter transformer | 23 | 23 | 3655.73 | 404879.8518
4609-Other exciter problems | 714 | 715 | 102306.17 | 4657938.7536
4610-Hydrogen cooling system piping and valves | 29 | 29 | 8863.13 | 423217.4157
4611-Hydrogen coolers | 24 | 24 | 4482.69 | 2795858.0197
4613-Hydrogen seals | 22 | 22 | 4603.3 | 732801.5069
4619-Other hydrogen system problems | 53 | 53 | 8263.48 | 354359.7042
4620-Air cooling system | 43 | 43 | 3565.99 | 138961.7863
4630-Liquid cooling system | 66 | 66 | 16198.92 | 606839.0037
4640-Seal oil system and seals A | 33 | 33 | 7898.32 | 500853.4305
4650-Other cooling system problems | 51 | 51 | 7159.73 | 217494.1004
4700-Generator voltage control | 193 | 193 | 27454.09 | 469661.3916
4710-Generator metering devices | 43 | 43 | 6735.94 | 122161.8952
4720-Generator synchronization equipment | 205 | 205 | 21476.2 | 382959.8739
4730-Generator current and potential transformers | 92 | 92 | 18919.41 | 2405892.9821
4740-Emergency generator trip devices | 209 | 211 | 29960.19 | 1464208.9729
4750-Other generator controls and metering problems | 316 | 318 | 39839.96 | 839767.0378
4800-Generator main leads | 28 | 28 | 7352.87 | 4088093.3752
4805-Generator Bus Duct Cooling System | 13 | 13 | 3178.26 | 570828.4975
4810-Generator output breaker | 410 | 413 | 46206.71 | 3630145.8035
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 5 | 5 | 1192.51 | 2780656.3021
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 5 | 5 | 339 | 8486.3333
4840-Inspection E | 88 | 100 | 4234.92 | 908173.3284
4841-Generator doble testing | 2 | 2 | 568 | 33067.3998
4842-Reactive and capability testing | 13 | 13 | 2918.42 | 471356.507
4850-Core monitor alarm | 2 | 2 | 152 | 2.5332
4860-Generator Neutral Grounding Equipment | 38 | 38 | 6696.23 | 2114834.8774
4899-Other miscellaneous generator problems | 356 | 360 | 50312.45 | 2910340.5344
5000-Inlet air ducts A | 22 | 22 | 1698.5 | 118797.0878
5001-Inlet air vanes / nozzles | 187 | 187 | 23673.4 | 262736.6942
5002-Inlet air filters A | 105 | 106 | 8265.17 | 145682.8252
5003-Inlet cone | 1 | 1 | 7 | 47.8333
5004-Inlet air chillers B | 99 | 99 | 1635.11 | 136094.678
5005-Inlet air evaporative coolers B | 53 | 55 | 1010.93 | 31732.9767
5006-Inlet air foggers B | 19 | 19 | 895.8 | 38289.5745
5009-Other inlet air problems A | 55 | 55 | 3829.44 | 423695.1589
5010-High pressure shaft D | 2 | 2 | 314 | 158253.3833
5011-High pressure bearings C | 9 | 9 | 498 | 18913.4665
5012-High pressure blades/buckets B | 19 | 19 | 2197.8 | 365600.6773
5013-Compressor casing and bolts | 5 | 5 | 1053 | 11037.8163
5014-Compressor diaphragms | 3 | 3 | 312.96 | 2021.4559
5015-Compressor seals | 3 | 3 | 445 | 3341.5166
5016-High pressure compressor bleed valves | 164 | 165 | 22873.6 | 172455.327
5017-Low pressure compressor bleed valves | 65 | 82 | 11035.69 | 72116.6361
5019-Other high pressure problems A | 10 | 10 | 1178.61 | 4569.0377
5021-Low pressure bearings D | 1 | 1 | 161 | 4733.4
5022-Low pressure blades/buckets A | 12 | 12 | 1027 | 171308.7166
5029-Other low pressure problems E | 13 | 13 | 1179.47 | 3885.6854
5035-Compressor Washing | 13 | 13 | 1401.24 | 6699.3467
5037-Inlet bleed heat valve | 51 | 51 | 6506.11 | 43112.6404
5039-Other compressor problems | 108 | 108 | 11531.55 | 1267670.7322
5040-Fuel tanks B | 5 | 5 | 245.12 | 2697.3652
5041-Fuel piping and valves A | 807 | 813 | 108961.97 | 1997374.4868
5042-Fuel nozzles/vanes B | 85 | 85 | 9420.92 | 251341.501
5043-Fuel filters A | 61 | 63 | 9797.14 | 69303.3478
5044-Liquid fuel oil pump A | 60 | 61 | 4098.8 | 90639.7857
5046-Liquid fuel oil transfer/forwarding pump B | 23 | 23 | 3551.01 | 19723.8765
5047-Liquid fuel purge system A | 47 | 47 | 5504.34 | 101155.9823
5048-Gas fuel system B | 661 | 671 | 81890.25 | 956006.3469
5049-Other fuel system problems B | 305 | 308 | 34326.03 | 1219031.8812
5050-Ignition system A | 279 | 281 | 33651.64 | 399055.4628
5051-Pilot fuel piping and valves A | 81 | 82 | 11213.8 | 70354.4263
5052-Pilot fuel nozzles/vanes B | 12 | 12 | 1522.5 | 4580.2979
5053-Pilot fuel filters A | 3 | 3 | 696 | 1790.2665
5054-Water Injection System (Gas Turbine) | 140 | 141 | 11339.97 | 191297.1008
5060-Atomizing air system B | 57 | 57 | 8152.35 | 96031.4937
5065-NOx water injection system including pumps | 137 | 138 | 10753.85 | 35374.0612
5066-NOx Steam Injection System | 25 | 25 | 6251.61 | 274045.8272
5070-Combustor casing A | 10 | 10 | 1575.21 | 287303.7382
5071-Combustor liner B | 18 | 18 | 2251 | 129386.9659
5072-Combustor caps B | 6 | 6 | 1066.3 | 25906.0829
5073-Flame scanners B | 106 | 107 | 10477.49 | 79497.3674
5074-Flashback including instruments | 52 | 52 | 7190.6 | 127644.6367
5075-Blade Path Temperature Spread A | 245 | 255 | 39373.65 | 386785.9524
5079-Other combustor problems B | 401 | 407 | 55037.92 | 793512.6453
5080-High pressure shaft C | 9 | 9 | 1807 | 2530285.183
5081-High pressure bearings D | 25 | 27 | 2064.2 | 88872.4192
5082-High pressure blades/buckets A | 18 | 18 | 1774.31 | 177797.4476
5083-High pressure nozzles/vanes A | 10 | 10 | 1033 | 157942.483
5084-High pressure casing/expansion joints | 8 | 8 | 544 | 58049.2332
5085-Interstage gas passages - HP | 12 | 12 | 1086.22 | 219117.9945
5086-High pressure shaft seals A | 4 | 4 | 124 | 64697
5087-Thrust Bearing | 13 | 13 | 1204.04 | 21354.1297
5088-Gas turbine cooling steam | 33 | 33 | 4514.87 | 86947.7731
5089-Other high pressure problems B | 22 | 22 | 745.7 | 61503.7098
5090-Low pressure shaft A | 3 | 3 | 138 | 438.5333
5091-Low pressure bearings A | 5 | 5 | 721.5 | 234283.4899
5092-Low pressure blades/buckets D | 26 | 26 | 5361 | 1245069.1154
5094-Low pressure casing/expansion joints A | 1 | 1 | 28.01 | 20279.7068
5096-Low pressure shaft seals | 1 | 1 | 100 | 100826.6666
5097-Other low pressure problems B | 11 | 11 | 756.34 | 1922.7765
5098-Expansion joints A | 6 | 6 | 384 | 217722.1999
5099-HP to LP coupling | 2 | 2 | 102 | 52371.5833
5100-Chamber A | 28 | 28 | 3114.05 | 350020.9177
5101-Hoods B | 4 | 4 | 225 | 3953.8166
5102-Vanes/nozzles A | 4 | 4 | 316 | 103954.2499
5103-Silencer B | 3 | 3 | 285.7 | 99062.13
5105-Diverter Dampers B | 11 | 11 | 1511.4 | 29366.8776
5106-Exhaust Stack | 11 | 11 | 1030.5 | 86668.9219
5108-High engine exhaust temperature A | 132 | 132 | 14783.85 | 180442.0549
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 250 | 250 | 30343.1 | 821116.1299
5110-Lube oil system - general | 266 | 267 | 20550.5 | 1254279.7813
5111-Lube oil pumps B | 102 | 102 | 10018.88 | 278376.7095
5112-Lube oil coolers B | 21 | 21 | 2231.8 | 54926.1724
5113-Lube oil valves/piping | 45 | 45 | 4083.34 | 295544.6597
5114-Lube oil filters | 8 | 8 | 632.9 | 3164.5415
5115-Oil vapor extractor | 19 | 19 | 1431.4 | 31435.1644
5116-Power Augmentation System Equipment B | 6 | 6 | 772.46 | 237700.62
5118-Power augmentation valves | 7 | 7 | 947 | 10241.1329
5119-Power augmentation controls | 6 | 6 | 373.9 | 1368.1015
5120-Hydraulic oil system A | 143 | 143 | 16491.24 | 254337.704
5121-Hydraulic oil system pumps | 31 | 31 | 3387.59 | 26798.3897
5122-Hydraulic oil system piping/valves | 55 | 55 | 6736.44 | 136187.5868
5130-Starting system (including motor) A | 391 | 392 | 46635.88 | 896479.3937
5140-Battery and charger system B | 10 | 10 | 774.15 | 10400.6581
5150-Turning gear and motor C | 66 | 66 | 5972.86 | 219007.8836
5151-Load gear compartment B | 1 | 1 | 45.7 | 573.535
5160-Cooling and seal air system B | 157 | 157 | 24417.18 | 239168.9944
5170-Cooling water system A | 67 | 67 | 5321.44 | 96750.352
5180-Anti-icing system A | 11 | 11 | 1074.2 | 3229.5696
5190-Other auxiliary system problems A | 168 | 172 | 20557.27 | 256371.0399
5200-Reduction gear B | 6 | 6 | 495.5 | 85818.6667
5201-Load shaft and bearings A | 11 | 11 | 1127.8 | 172438.1529
5206-Gas Turbine Clutch | 18 | 18 | 1328.68 | 127205.3879
5210-Intercoolers A | 15 | 15 | 2623.57 | 5516.1577
5220-Regenerators A | 1 | 1 | 235 | 1605.8333
5230-Heat shields C | 1 | 1 | 126 | 2751
5240-Fire detection and extinguishing system B | 203 | 203 | 24072.73 | 882388.1409
5241-Fire in unit A | 6 | 6 | 1049 | 301931.5495
5245-Gas Turbine Control System - data highway | 67 | 67 | 8210.75 | 44142.4331
5246-Gas Turbine Control System - hardware problems (including card failure) | 324 | 324 | 38031.11 | 564947.7139
5247-Gas Turbine Control System - internal and termination wiring | 69 | 69 | 7991.79 | 191844.0417
5248-Gas Turbine Control System - logic problems | 122 | 125 | 16741.94 | 148693.4429
5249-Gas Turbine Control System - upgrades | 14 | 14 | 2085 | 41538.2992
5250-Other Controls and instrumentation Problems A | 539 | 556 | 57502.55 | 769162.8548
5255-Computer | 34 | 34 | 2807.2 | 27442.7488
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 11 | 11 | 1218 | 100915.2829
5261-Gas turbine/compressor washing | 14 | 14 | 1297 | 14951.2405
5262-Gas turbine exchange | 6 | 6 | 497.46 | 47744.2556
5269-Combustion inspection (CI) | 2 | 2 | 207.61 | 11886.9083
5270-Hot end inspection B | 5 | 5 | 1125.7 | 237297.2597
5272-Boroscope inspection A | 32 | 32 | 3209.48 | 867656.3734
5274-General unit inspection A | 18 | 18 | 2417.34 | 299276.2069
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 41 | 41 | 3249.9 | 315915.8789
5285-Gas turbine vibration | 264 | 266 | 22947.96 | 3464346.1469
5286-Gas Turbine lockout cause by OEM specifications | 13 | 13 | 1203.3 | 8576.0662
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 16 | 19 | 906 | 1214.5663
5295-Synchronous condenser equipment A | 1 | 1 | 197.4 | 88.83
5298-Main gas filter | 4 | 4 | 785 | 9346.1664
5299-Other miscellaneous gas turbine problems | 487 | 489 | 51927.72 | 1556983.5911
5400-Inlet air ducts B | 2 | 2 | 109 | 4435.7333
5401-Inlet air vanes/noozles | 21 | 21 | 2362.53 | 22394.8338
5402-Inlet air filters B | 4 | 4 | 222.5 | 674.8832
5404-Inlet air chillers A | 33 | 33 | 279.9 | 34246.3483
5405-Inlet air evaporative coolers A | 6 | 6 | 108.4 | 124.4666
5406-Inlet air foggers A | 2 | 2 | 21.4 | 5423.7683
5409-Other inlet air problems B | 12 | 12 | 515.9 | 5393.4815
5412-High pressure blades/buckets C | 19 | 19 | 740 | 67344.2497
5413-Other high pressure problems D | 30 | 30 | 840.1 | 82073.0798
5414-Compressor diaphragms/vanes | 4 | 4 | 143.8 | 1529.92
5422-Low pressure blades/buckets C | 3 | 3 | 120.2 | 317210.9833
5429-Other low pressure problems D | 6 | 6 | 250.7 | 4700.2116
5435-Jet Engine Compressor Washing | 1 | 1 | 4 | 662.6
5439-Jet engine other compressor problems | 23 | 23 | 796.56 | 8514.9511
5441-Fuel piping and valves B | 117 | 118 | 5219.01 | 122607.389
5442-Fuel nozzles/vanes A | 5 | 5 | 201 | 44215.3832
5443-Fuel filters B | 5 | 5 | 253 | 1715.5666
5444-Liquid fuel oil pump B | 11 | 11 | 339.55 | 4084.0866
5445-Liquid fuel oil transfer/forwarding pump A | 12 | 12 | 407 | 9724.0498
5446-Liquid fuel purge system B | 10 | 10 | 531.8 | 7097.8365
5447-Gas fuel system A | 195 | 200 | 10441.02 | 81063.6205
5449-Other fuel system problems A | 132 | 137 | 5365.92 | 112036.4035
5450-Ignition system B | 42 | 42 | 2220.34 | 34894.6756
5451-Pilot fuel piping and valves B | 9 | 9 | 470.04 | 1708.0058
5452-Pilot fuel nozzles/vanes A | 1 | 1 | 21 | 519.75
5454-Water injection system (Jet Engine) | 96 | 97 | 4023.61 | 21003.6147
5455-Fuel nozzle/vane cooling air system | 2 | 2 | 132.66 | 755.8796
5460-Atomizing air system A | 2 | 2 | 46 | 1069.5
5470-Combustor casing B | 1 | 1 | 29 | 13.05
5471-Combustor liner A | 3 | 3 | 185 | 136.2332
5473-Flame scanners A | 29 | 29 | 1903.74 | 14698.5736
5474-Flashback (including instrumentation) | 7 | 7 | 1122.7 | 92500.758
5475-Blade Path Temperature Spread B | 52 | 53 | 6246.27 | 37239.0787
5479-Other combustor problems A | 19 | 19 | 849.55 | 35145.7155
5481-High pressure bearings A | 3 | 3 | 276 | 20305.3666
5482-High pressure blades/buckets D | 4 | 4 | 164.5 | 148965.25
5483-High pressure nozzles/vanes B | 1 | 1 | 12.9 | 3.655
5486-High pressure shaft seals B | 2 | 2 | 113 | 4171.5833
5487-Thrust Bearing/jet | 2 | 2 | 109.4 | 421.3533
5489-Other high pressure problems C | 6 | 6 | 430.5 | 46898.5499
5492-Low pressure blades/buckets B | 4 | 4 | 239.7 | 184635.3599
5493-Low pressure nozzles/vanes A | 3 | 3 | 124 | 189188.5333
5497-Other low pressure problems C | 1 | 1 | 65.7 | 14.235
5499-Shaft seals A | 1 | 1 | 25 | 26261.6666
5505-Diverter Dampers A | 5 | 5 | 309.86 | 2579.8945
5508-High engine exhaust temperature B | 40 | 41 | 1701.1 | 42640.3627
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 40 | 41 | 2257.9 | 37439.5825
5510-Lube oil system A | 247 | 252 | 11064.16 | 153918.2343
5516-Power Augmentation System Equipment A | 21 | 21 | 647.8 | 98590.1197
5520-Hydraulic oil system B | 47 | 47 | 2984.99 | 23156.209
5530-Starting system (including motor) B | 75 | 76 | 3535.23 | 123121.3324
5540-Battery and charger system A | 4 | 4 | 165.5 | 443.2416
5550-Turning gear and motor B | 11 | 11 | 1061.3 | 37210.6512
5551-Load gear compartment A | 1 | 1 | 52 | 602.3333
5560-Cooling and seal air system A | 37 | 37 | 2403.9 | 10905.8127
5570-Cooling water system B | 21 | 21 | 290.4 | 835.9766
5580-Anti-icing system B | 21 | 21 | 876.7 | 6432.0264
5590-Other auxiliary system problems B | 54 | 54 | 2764.6 | 25525.2289
5601-Load shaft and bearings B | 1 | 1 | 45 | 42.75
5605-Main coupling between the turbine and generator B | 1 | 1 | 50 | 1340
5606-Jet Engine Clutch | 4 | 4 | 177.8 | 966.9333
5610-Intercoolers B | 3 | 3 | 336 | 4567.7333
5630-Heat shields A | 6 | 6 | 125 | 2419.8833
5640-Fire detection and extinguishing system A | 67 | 67 | 3040.05 | 18307.0359
5641-Fire in unit B | 1 | 1 | 50 | 1165.8333
5645-Jet Engine Control System - data highway | 34 | 34 | 1591.15 | 6427.5677
5646-Jet Engine Control System - hardware problems (including card failure) | 106 | 107 | 4657.2 | 49181.3651
5647-Jet Engine Control System - internal and termination wiring | 42 | 45 | 1860.6 | 8139.8594
5648-Jet Engine Control System - logic problems | 53 | 54 | 2242.65 | 28843.6818
5649-Jet Engine Control System - upgrades | 3 | 3 | 264.3 | 144.4499
5650-Other Controls and instrumentation Problems B | 165 | 166 | 6707.57 | 160418.9628
5661-Engine/compressor washing | 3 | 3 | 134 | 480.7667
5662-Engine exchange | 2 | 2 | 58 | 5968.6333
5665-Engine shafts and bearings | 2 | 2 | 88.5 | 32643.7083
5670-Hot end inspection A | 2 | 2 | 130 | 2139.5833
5672-Boroscope inspection B | 7 | 7 | 573.5 | 155659.9914
5674-General unit inspection B | 12 | 12 | 459.45 | 10282.0644
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 42 | 42 | 1786.49 | 37217.7279
5685-Engine vibration | 131 | 132 | 6263.8 | 241354.1796
5686-Jet Engine lockout cause by OEM specifications | 12 | 12 | 1117.2 | 1804.8663
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 18 | 19 | 245 | 467.8499
5695-Synchronous condenser equipment B | 4 | 4 | 151 | 736.7166
5699-Other miscellaneous jet engine problems | 127 | 131 | 4847.73 | 145626.6532
5710-Cylinders | 7 | 7 | 82.04 | 470.95
5711-Cylinder heads | 24 | 26 | 370.06 | 1296.6269
5730-Intake valves | 1 | 1 | 9.04 | 328.4533
5740-Turbo charger | 5 | 5 | 55.16 | 9452.308
5790-Vibration | 1 | 1 | 10.5 | 514.5
5799-Other engine problems | 39 | 39 | 280.7 | 16645.3343
5800-Lube oil system C | 5 | 5 | 30.58 | 180.2253
5805-Cooling system | 17 | 20 | 193.39 | 1667.5341
5815-Fuel system | 18 | 18 | 248.5 | 4425.5916
5820-Start system | 22 | 23 | 201.39 | 387.5148
5849-Other engine auxiliaries problems | 20 | 20 | 243.77 | 3584.8802
5850-Governor | 3 | 3 | 15.32 | 1157.2625
5855-Engine control system | 33 | 38 | 392.17 | 3298.742
5870-Other engine control problems | 3 | 3 | 29.04 | 5515.2173
5895-Inspection C | 2 | 2 | 29.04 | 1577.0693
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 55 | 72 | 1187.56 | 5511.8678
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 38 | 38 | 5597.07 | 94734.3876
6005-HP Evaporator tubes | 20 | 20 | 2764.57 | 510944.6232
6007-LP Evaporator tubes | 10 | 10 | 932.33 | 87677.475
6010-HP superheater | 26 | 26 | 2412.3 | 148558.5492
6011-HP reheater | 6 | 6 | 1264.53 | 182444.0432
6012-HP economizer | 30 | 30 | 4911.76 | 473160.4546
6020-IP superheater | 4 | 4 | 424 | 17204.5165
6021-IP reheater | 16 | 16 | 2455.31 | 143942.7703
6022-IP economizer | 8 | 8 | 2303 | 100768.9998
6031-LP superheater | 1 | 1 | 174 | 4500.7999
6032-LP economizer | 8 | 8 | 1373.21 | 24254.1563
6090-Other HRSG tube Problems | 12 | 12 | 2795.28 | 148173.9458
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 4 | 4 | 565 | 39076.3331
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 25 | 25 | 4937.3 | 217866.8991
6111-HP steam relief/safety valves | 9 | 9 | 1131 | 25974.7997
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 39 | 39 | 6226.65 | 120250.2784
6113-Other HP steam system problems | 17 | 17 | 3318.31 | 112163.8226
6114-HP steam isolation/boundary valves | 38 | 38 | 7371.57 | 117090.6164
6121-IP steam relief/safety valves | 2 | 2 | 812 | 14378.6499
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 9 | 9 | 1723.02 | 14419.1726
6123-Other IP steam system problems | 16 | 16 | 3873 | 69024.4155
6124-IP steam isolation/boundary valves | 16 | 16 | 4532.64 | 66470.2309
6131-LP steam relief/safety valves | 1 | 1 | 358 | 23562.3664
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 18 | 18 | 3606.2 | 11079.5841
6133-Other LP steam system problems | 11 | 11 | 2103 | 22704.9326
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 43 | 43 | 7176.1 | 129041.8757
6135-LP steam isolation/boundary valves | 3 | 3 | 341 | 962.9832
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 4 | 4 | 669.7 | 14364.0264
6141-HP Desuperheater/attemperator valves | 34 | 34 | 4947.82 | 102307.7561
6142-HP Desuperheater/attemperator spray nozzles | 1 | 1 | 42 | 105
6143-HP Desuperheater/attemperator drums | 2 | 2 | 305 | 164930.9999
6144-Other HP desuperheater/attemperator problems | 25 | 25 | 6053.6 | 32103.3613
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 6 | 6 | 949 | 11065.5496
6146-IP Desuperheater/attemperator valves | 10 | 10 | 1273 | 11239.5496
6147-IP Desuperheater/attemperator spray nozzles | 2 | 2 | 938.4 | 1266.84
6149-Other IP desuperheater/attemperator problems | 1 | 1 | 228.73 | 857.7375
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 2 | 2 | 268 | 7942.3
6161-HP Startup bypass system valves | 51 | 51 | 9631.48 | 183510.6103
6163-Other HP startup bypass system problems | 4 | 4 | 589 | 32807.4166
6164-HP Startup bypass instrumentation and controls | 53 | 54 | 11709.93 | 133667.6626
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 4 | 4 | 683.5 | 27285.4248
6171-IP Startup bypass system valves | 29 | 29 | 5487.46 | 55815.9817
6174-IP Startup bypass instrumentation and controls | 9 | 9 | 1814.34 | 12683.81
6181-LP Startup bypass system valves | 4 | 4 | 1013.5 | 3408.7413
6183-Other LP startup bypass system problems | 4 | 4 | 816.4 | 10152.2698
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 105 | 107 | 15510.99 | 85022.6994
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 83 | 83 | 10911.51 | 247777.9054
6399-Other coal gasification equipment problems | 32 | 32 | 2100 | 118744.5825
6410-Steam wells/steam field piping problems | 15 | 15 | 257 | 4856.9166
6415-Low steam pressure | 1 | 1 | 16 | 17.0667
6420-Condensate reinjection system | 21 | 21 | 114 | 5940.8
6499-Geothermal | 5 | 5 | 83 | 111.3166
7000-Shaft B | 4 | 4 | 544.9 | 43125.1215
7001-Shaft packing | 41 | 41 | 4151.71 | 171691.6812
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 47 | 48 | 5415.77 | 722782.1762
7007-Bearings A | 43 | 43 | 3284.73 | 624706.3775
7008-Bearing cooling system B | 43 | 43 | 4247.88 | 49613.027
7009-Bearing Oil System | 79 | 79 | 7042.24 | 1150778.069
7011-Other runner problems | 6 | 6 | 647.43 | 242075.8638
7014-Blade or bucket cracking | 1 | 1 | 32.93 | 38967.7155
7020-Nozzle assembly | 2 | 2 | 161.7 | 2583.1574
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 56 | 56 | 2310.8 | 707476.2207
7040-Turbine overhaul | 2 | 2 | 118 | 8767.3333
7050-Turbine governor | 158 | 171 | 10056.31 | 1229846.6802
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 38 | 39 | 4324.31 | 340319.5979
7053-Governor Oil System | 82 | 82 | 6862.01 | 453946.7701
7099-Other turbine problems | 164 | 167 | 11152.91 | 1363367.1089
7100-Upper reservoir dams and dikes | 14 | 14 | 1048.5 | 11198.5955
7101-Lower reservoir dams and dikes | 1 | 1 | 2.2 | 128.5167
7110-Intake channel or flume (including trash racks) | 124 | 125 | 5355.38 | 380527.1349
7111-Intake tunnel | 19 | 19 | 1676.23 | 50858.6336
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 17 | 17 | 524.8 | 14392.2332
7120-Headgates | 23 | 23 | 1310.89 | 69866.542
7121-Shutoff valves | 25 | 25 | 3227.62 | 139338.5434
7123-Shutoff valve bypass line and valve | 14 | 15 | 2009.12 | 313778.621
7124-Penstock | 26 | 26 | 1548.37 | 251015.8174
7130-Spiral case | 1 | 1 | 25 | 509.5833
7140-Wicket gate assembly | 22 | 22 | 1009.24 | 203790.536
7141-Wicket gate operating mechanism or positioner | 36 | 36 | 2938.79 | 147504.1131
7142-Wicket gate shear pin | 122 | 123 | 8440.9 | 359171.3618
7160-Pressure regulating valve | 10 | 10 | 506.39 | 43290.1847
7161-Pressure regulating valve operator or positioner | 3 | 3 | 70.6 | 352.85
7162-Relief valve and vacuum breakers | 1 | 1 | 18 | 87
7170-Draft tube | 12 | 12 | 1112.67 | 111907.4924
7180-Tailrace | 27 | 27 | 869.5 | 26727.1081
7181-Tail water depressing equipment | 12 | 12 | 1393.41 | 14986.0193
7190-Dewatering and rewatering equipment | 7 | 7 | 97.88 | 411.03
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 143 | 143 | 3628.82 | 235591.6387
7200-Major overhaul (use for non-specific overhaul only; see page B-1) B | 2 | 2 | 101.25 | 6745.7624
7201-Inspection A | 4 | 4 | 397.94 | 47595.3242
7210-Canals (including siphons; radial gates; and spills) | 3 | 3 | 45 | 4175
7220-Unit out of service due to common penstock with unit under repair | 1 | 1 | 293 | 68.3666
7230-Pony motor (pumped storage units only) | 2 | 2 | 675 | 1989.6664
7240-Powerhouse Substructure | 3 | 3 | 73.75 | 191900.3541
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 40 | 40 | 3303.9 | 29241.4197
7300-Routine Hydro Planned Outage (reoccuring schedule) | 1 | 1 | 27 | 45.9
7810-Shaft A | 1 | 1 | 58 | 4934.8333
7820-Bearings B | 6 | 6 | 186.5 | 87780.6082
7830-Blades | 12 | 12 | 323.7 | 222297.7282
7840-Discs | 7 | 7 | 80 | 659519.3333
7860-Nozzles/vanes | 2 | 2 | 86 | 6503.75
7880-Exhaust diffusers | 2 | 2 | 75 | 25647.5
7890-Seal oil system and seals B | 3 | 3 | 250.5 | 14174.0916
7910-Outer exhaust casing | 1 | 1 | 20 | 4016.6667
7920-Lube oil system B | 20 | 20 | 964.6 | 7575.533
7930-Controls and instrumentation A | 21 | 21 | 1686.24 | 21520.7875
7950-Major overhaul B | 2 | 2 | 66 | 18407.4
7960-Other expander turbine problems | 8 | 8 | 470.93 | 42204.3495
8000-Chemical feed storage; mill feeders; and conveyors | 3 | 3 | 198.02 | 3606.6063
8003-Bucket elevators | 1 | 1 | 66 | 8496.4
8010-Crushers/mills | 25 | 25 | 3671.62 | 26611.861
8020-Mill slurry tanks supply problems | 6 | 6 | 1231.64 | 11553.4343
8040-Slurry transfer pumps and motors | 7 | 7 | 1207.93 | 2138.4455
8050-Chemical unavailability | 1 | 1 | 26.3 | 578.1617
8099-Other chemical supply problems | 5 | 5 | 526.13 | 6313.56
8100-Scrubber/absorber tower or module | 123 | 123 | 18986.73 | 10239922.2793
8110-Spray nozzles | 7 | 7 | 1529.7 | 47882.0157
8120-Spray pumps and motors | 15 | 15 | 930 | 16084.8664
8125-Scrubber recycle (liquid) pumps | 24 | 24 | 4982.95 | 55566.9577
8127-Scrubber recycle (liquid) pump motors | 7 | 7 | 798.19 | 3528.5281
8130-Recirculation tanks including agitators | 4 | 4 | 292 | 6128.8665
8140-Reaction tanks including agitators | 17 | 17 | 2149 | 129523.9493
8160-Mist eliminators/demisters and washdown | 102 | 102 | 11014.63 | 385942.7812
8199-Other scrubber problems | 35 | 35 | 5028 | 47680.2483
8200-Piping | 15 | 15 | 2050 | 17306.1325
8210-Valves | 11 | 11 | 1919.43 | 11670.9165
8220-Strainers or filters | 2 | 2 | 16.2 | 3764.4833
8230-Ducting | 15 | 15 | 3802.71 | 283214.6173
8235-Demister | 7 | 7 | 189 | 46.8
8250-Dampers other than bypass | 2 | 2 | 273.99 | 536.9824
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 28 | 28 | 4665.59 | 122705.9263
8261-Scrubber booster I.D. fan drive | 12 | 12 | 2871.18 | 34402.3213
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 14 | 14 | 3275 | 436528.516
8264-Scrubber booster I.D. fan blades (fan specific to the scrubber) | 8 | 8 | 2469 | 188984.8496
8265-Scrubber ID fan dampers | 6 | 6 | 1291.14 | 10452.2128
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 23 | 23 | 1945.12 | 21463.5684
8271-Scrubber booster F.D. fan drive | 8 | 8 | 1131.7 | 19407.4447
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 8 | 8 | 2069 | 69452.3823
8275-Scrubber FD fan dampers | 1 | 1 | 49 | 260.5166
8280-Reagent feed piping | 20 | 20 | 4001.4 | 104353.0021
8299-Other piping; ducting; damper; and fan problems | 6 | 6 | 715 | 126910.6665
8325-Ash disposal problems | 3 | 3 | 735 | 5843
8330-Dewatering equipment (thickener; centrifuge; etc.) | 34 | 34 | 9019 | 488876.0804
8349-Other waste disposal and recovery problems | 3 | 3 | 1171.52 | 77303.7407
8399-Solids conveying and mixing system problems | 5 | 5 | 1592 | 16980.9657
8400-Scrubber gas discharge reheaters - general | 1 | 1 | 15 | 248.75
8404-Scrubber gas discharge reheaters - tube leaks | 1 | 1 | 92 | 809.6
8410-Scrubber instruments and controls | 29 | 29 | 4464.56 | 44463.8773
8415-Liquid level controls | 2 | 2 | 964 | 11247.6998
8425-Miscellaneous mechanical failures | 6 | 6 | 2113 | 9605.9992
8426-Miscellaneous electrical failures | 16 | 16 | 3327.82 | 18084.5807
8430-Stack damage related to scrubber system | 1 | 1 | 93.92 | 1463.5866
8460-Testing | 3 | 3 | 174.63 | 718.91
8470-SO2 monitor | 1 | 1 | 262 | 414.8332
8499-Other miscellaneous wet scrubber problems | 119 | 119 | 11695.33 | 484199.5735
8500-Slurry storage and feed tanks | 4 | 4 | 324 | 5214.95
8502-Weigh feeders | 1 | 1 | 95 | 10864.8333
8503-Screw conveyors | 7 | 7 | 2095.62 | 60781.186
8504-Mills/slakers | 1 | 1 | 102 | 705.4999
8505-Scalping screens | 2 | 2 | 183 | 3755.3166
8506-Slurry pipelines | 8 | 8 | 396 | 12298.0166
8507-Reagent uploading and transfer systems | 5 | 5 | 861 | 7869.883
8508-Reagent unavailability | 5 | 5 | 163.8 | 1054.6366
8510-Slurry mixers and agitators | 6 | 6 | 543 | 8931.6832
8520-Slurry transfer pumps and motors | 6 | 6 | 475.6 | 3068.1598
8521-Reagent/slurry problems | 8 | 8 | 579 | 1749.7665
8522-Piping | 7 | 7 | 853 | 8563.9497
8523-Valves | 3 | 3 | 113 | 1034.3333
8524-Strainers or filters | 11 | 11 | 1830.32 | 193762.1179
8525-Ducting | 6 | 6 | 820.87 | 126216.131
8526-Dampers | 4 | 4 | 611 | 1110.9832
8527-Other piping; ducting; and damper problems | 3 | 3 | 145 | 17506.6666
8528-Dry scrubber instruments and controls | 6 | 6 | 460 | 3236.9164
8529-Gas dispersers | 7 | 7 | 1873.3 | 210489.6416
8530-Spray towers | 3 | 3 | 325.99 | 3796.4356
8531-Spray machine/atomizer | 43 | 43 | 3367.9 | 30609.6991
8532-Spray machine/atomizer motors | 3 | 3 | 177.2 | 1217.3466
8533-Spray machine/atomizer lubrication systems | 7 | 7 | 1532.6 | 6397.0862
8534-Spray machine/atomizer vibration problems | 14 | 14 | 1566.1 | 17141.6029
8535-Fly ash conveyors | 9 | 9 | 854.92 | 17060.9372
8538-Recycle storage and feed tanks including agitators | 11 | 11 | 220 | 16741.9999
8539-Recycle slurry transfer pumps | 1 | 1 | 96 | 76.8
8544-Mechanical failures | 4 | 4 | 489 | 3870.3833
8545-Electrical failures | 7 | 7 | 2374 | 67186.9496
8547-Inspection | 24 | 25 | 1523 | 3965.1997
8548-Testing | 5 | 5 | 1049 | 5605.4995
8549-Other dry scrubber problems | 34 | 34 | 5736.1 | 225663.835
8550-Electrostatic precipitator fouling | 103 | 103 | 19394.91 | 490407.3284
8551-Electrostatic precipitator field out of service | 217 | 220 | 23661.83 | 422361.7747
8560-Electrostatic precipitator problems | 207 | 207 | 25796.41 | 413598.2863
8570-Mechanical precipitator fouling | 7 | 7 | 715 | 1374854.4164
8580-Mechanical precipitator problems | 8 | 8 | 920 | 4356.8329
8590-Other precipitator problems | 41 | 42 | 2407.37 | 79897.1553
8600-Flue gas additives (furnace injection) | 8 | 8 | 962.6 | 11972.7464
8601-SO3 mitigation | 31 | 31 | 5639 | 24330.1813
8620-Mercury Abatement | 169 | 189 | 29245.11 | 1354712.2524
8650-Baghouse systems; general | 285 | 285 | 14202.05 | 697954.7444
8651-Bag failures and rebagging | 112 | 112 | 6346.63 | 345607.3102
8652-Shakers and rappers | 2 | 2 | 54 | 2552.1667
8653-Inflation and deflation fans and motors | 2 | 2 | 189 | 416.0499
8654-Baghouse booster fans and motors | 13 | 13 | 2352 | 80622.2827
8655-Structural duct work and dampers | 4 | 4 | 943 | 179431.9827
8656-Controls and instrumentation B | 45 | 45 | 4451.3 | 91316.842
8657-Ash handling system and hoppers | 29 | 30 | 4586.16 | 339177.1184
8658-Slurry system from precipitators | 1 | 1 | 80 | 3252
8670-Emission monitors (other than CEMS) A | 2 | 2 | 596 | 20267.1333
8699-Other miscellaneous pollution control equipment problems | 67 | 67 | 7277.2 | 155465.7394
8700-CEMS Certification and Recertification | 28 | 28 | 1958.81 | 25642.3242
8710-SO2 analyzer problems | 2 | 2 | 272 | 346.7999
8720-NOx analyzer problems | 60 | 60 | 5316.8 | 58447.1976
8730-CO analyzer problems | 12 | 12 | 1282.4 | 67753.4695
8740-CO2 analyzer problems | 9 | 9 | 628.6 | 8380.9614
8750-O2 analyzer problems | 19 | 20 | 2701.07 | 33517.5338
8760-Opacity monitor problems | 20 | 20 | 2865.9 | 78104.1489
8770-Flow monitor problems | 10 | 10 | 468.8 | 2978.8398
8780-Data acquisition system problems | 49 | 49 | 5063.06 | 263045.6075
8790-Miscellaneous CEMS problems | 199 | 201 | 13561.62 | 396321.2689
8800-SNCR NOx Reagent | 2 | 2 | 88 | 243.4666
8802-SNCR NOx Control system | 29 | 29 | 1623.38 | 8885.1252
8803-Sncr Performance Testing | 1 | 1 | 280 | 2310
8809-Other SNCR NOx problems | 31 | 31 | 1635.45 | 42336.8693
8810-SCR NOx Reactor | 16 | 16 | 1485.6 | 5763.4641
8811-SCR NOx Reagent | 6 | 6 | 628 | 11336.0664
8812-SCR NOxCatalyst | 40 | 42 | 1406.57 | 259921.7583
8813-SCR NOx Injection grid piping/valves | 34 | 34 | 2190.99 | 962162.1394
8814-SCR NOx Catalyst support material | 1 | 1 | 39.9 | 12.635
8815-SCR NOx Soot blowers | 1 | 1 | 99.2 | 7316
8816-SCR NOx Plugging | 44 | 44 | 1844.96 | 156499.8951
8817-SCR NOx Control system | 78 | 78 | 6896.85 | 108517.2831
8820-SCR NOx Ammonia injection grid piping/valves | 33 | 33 | 3785.73 | 22957.696
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 21 | 21 | 2130.85 | 16681.5221
8822-SCR NOx Ammonia air blowers | 29 | 30 | 3475.46 | 28402.8724
8823-SCR NOx Other ammonia system problems | 129 | 130 | 12800.22 | 147492.6923
8825-Other SCR NOx problems | 135 | 135 | 7858.96 | 315017.9751
8831-CAH NOx Support materials | 3 | 3 | 267 | 2537.6833
8832-CAH NOx Plugging | 5 | 5 | 105 | 18001.8
8835-CAH NOx Other CAH problems | 2 | 2 | 304 | 2411.4
8840-CO Active catalyst | 9 | 9 | 364 | 6947.3999
8841-CO Support materials | 4 | 4 | 311 | 3081.6832
8842-CO Plugging | 17 | 17 | 78 | 968.4166
8845-Other CO reduction problems | 99 | 99 | 3809.7 | 131229.2556
9000-Flood | 180 | 180 | 2940.21 | 2110710.9967
9010-Fire; not related to a specific component | 97 | 97 | 8664.44 | 407445.0663
9020-Lightning | 128 | 128 | 17825.51 | 483972.6246
9030-Earthquake | 4 | 4 | 166 | 584.15
9031-Tornado | 3 | 3 | 127.68 | 1549.184
9035-Hurricane | 55 | 55 | 17867.92 | 1060901.2671
9036-Storms (ice; snow; etc) | 162 | 163 | 18185.12 | 856763.6233
9040-Other catastrophe | 22 | 22 | 2515.52 | 25590.0495
9110-Core coastdown (nuclear) | 1 | 1 | 46.6 | 253.1933
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 804 | 1032 | 78360.71 | 7193946.175
9131-Lack of fuel: Contract or Tariff allows for interruption | 705 | 890 | 96002.1 | 4744632.5153
9132-Wet Fuel - Biomass | 241 | 245 | 1545.65 | 12492.2871
9134-Fuel conservation | 144 | 146 | 7833.5 | 277658.9878
9135-Lack of water (hydro) | 2203 | 2439 | 31792.38 | 1559051.1001
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 27 | 34 | 2097 | 31498.0832
9137-Ground water or other water supply problems | 16 | 16 | 1761.17 | 102743.3285
9140-Plant modifications to burn different fuel (not regulatory mandated) | 1 | 1 | 17.5 | 5.25
9160-Other economic problems | 14 | 16 | 2867.8 | 26436.1163
9181-Economic (for internal use at plants only) | 4 | 4 | 1800.25 | 5274.4556
9182-Economic (for internal use at plants only) | 27 | 27 | 14464.17 | 36021.6079
9200-High ash content | 284 | 397 | 31604.45 | 303394.3285
9201-High ash content ? (not outside management control) | 43 | 43 | 7148 | 429419.1809
9205-Poor quality natural gas fuel; low heat content | 7 | 7 | 792.8 | 31022.1131
9211-Low grindability (not outside management control) | 3 | 3 | 153.2 | 1098.9733
9220-High sulfur content | 9 | 9 | 1373.5 | 9978.9994
9221-High sulfur content ? (not outside management control) | 1 | 1 | 430 | 4128
9230-High vanadium content | 3 | 3 | 37 | 443.3833
9240-High sodium content | 21 | 21 | 2091.52 | 35691.7825
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 352 | 355 | 9501.47 | 162314.4288
9251-Low Btu Coal From Contract For Low Btu Coal | 80 | 81 | 3127.6 | 215988.1656
9260-Low Btu oil | 1 | 1 | 110 | 77
9261-Low Btu oil (not outside management control) | 3 | 3 | 146.4 | 1163.16
9270-Wet coal | 1119 | 1128 | 138534.51 | 1738541.9292
9271-Wet coal (not outside management control) | 915 | 921 | 114272.08 | 1400051.2067
9272-Wet Fuel (other than coal) | 7 | 7 | 30.4 | 163.73
9280-Frozen coal | 28 | 28 | 4475.17 | 33300.1407
9281-Frozen coal (not outside management control) | 13 | 13 | 1040.2 | 6029.5031
9290-Other fuel quality problems | 354 | 355 | 26433.98 | 3051598.1595
9291-Other fuel quality problems (not outside management control) | 190 | 190 | 8832 | 200921.373
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 1084 | 1097 | 91713.8 | 2926350.2545
9305-Ash disposal problem | 5 | 5 | 2484 | 190166.3492
9310-Operator training | 5 | 5 | 562 | 23056.6667
9320-Other miscellaneous external problems | 935 | 1104 | 50427.02 | 5488282.2215
9340-Synchronous Condenser Operation | 3 | 3 | 267.1 | 132.8841
9345-Pumping Operations | 3 | 3 | 1509.2 | 3834.228
9350-Public Safety/River Rescue | 59 | 65 | 1003.7 | 7375.1716
9504-Regulatory (environmental) proceedings and hearings - regulatory agency initiated | 4 | 4 | 554 | 178889.7667
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 4 | 4 | 1996 | 4371240
9520-Oil spill in Gulf of Mexico | 2 | 2 | 16 | 7680
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 69 | 69 | 2630.51 | 370050.9589
9600-SO2 stack emissions (fossil) | 58 | 58 | 9519.56 | 460917.4845
9610-NOx stack emissions (fossil) | 117 | 118 | 5553.66 | 252775.8689
9613-NOx stack emissions (gas turbine) | 185 | 197 | 13963.5 | 253598.4202
9614-NOx stack emissions (jet engines) | 56 | 56 | 2022.85 | 19166.1651
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 1 | 1 | 7 | 4.55
9616-CO stack emissions | 191 | 192 | 14701.28 | 448615.2917
9620-Particulate stack emissions (fossil) | 50 | 50 | 7933.34 | 314596.4442
9623-Particulate stack emissions (gas turbine) | 2 | 2 | 49.8 | 243.19
9630-Opacity (fossil) | 353 | 356 | 35876.88 | 620796.8524
9634-Opacity (jet engines) | 1 | 1 | 42 | 259.7
9650-Other stack or exhaust emissions (fossil) | 253 | 266 | 14415.3 | 188076.3418
9653-Other stack or exhaust emissions (gas turbine) | 44 | 44 | 4061 | 178134.2971
9654-Other stack or exhaust emissions (jet engines) | 6 | 6 | 330.5 | 788.7798
9656-Other stack or exhaust emissions testing - fossil | 35 | 35 | 5960.63 | 262378.6486
9657-Other stack or exhaust emissions testing - gas turbine | 13 | 13 | 1026.05 | 21300.0271
9658-Other stack or exhaust emissions testing - jet engines | 1 | 1 | 18.4 | 47.5333
9660-Thermal discharge limits (fossil and nuclear) | 50 | 50 | 4254.5 | 85456.9134
9663-Thermal discharge limits (gas turbine) | 30 | 30 | 952.13 | 11548.0485
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 53 | 53 | 4173.41 | 333516.1142
9693-Other miscellaneous operational environmental limits (gas turbines) | 73 | 74 | 2744.72 | 61214.813
9694-Other miscellaneous operational environmental limits (jet engines) | 58 | 61 | 1217.52 | 45862.4434
9696-Other miscellaneous operational environmental limits (hydro and PS) | 33 | 33 | 1208.35 | 62299.8654
9700-OSHA-related retrofit or inspection | 1 | 1 | 717 | 528918.9498
9720-Other safety problems | 53 | 53 | 8326.17 | 2662991.2772
9900-Operator error | 451 | 451 | 105676.09 | 960407.4564
9910-Maintenance personnel error | 154 | 154 | 25753.21 | 187594.1295
9920-Contractor error | 88 | 88 | 19095.8 | 824369.1427
9930-Operating procedure error | 54 | 54 | 12792.44 | 177651.1637
9940-Maintenance procdure error | 27 | 27 | 5453.04 | 70447.4514
9950-Contractor procedure error | 6 | 6 | 383.75 | 1737.6166
9960-Staff shortage | 13 | 15 | 1711.6 | 17043.3399
9997-NERC Reliability Standards requirements | 20 | 20 | 1330.88 | 21085.0993
9998-Black Start testing | 8 | 8 | 769 | 5092.8832
9999-Total unit performance testing (use appropriate codes for individual component testing) | 202 | 220 | 8263.15 | 1822046.4038
Total Result | 66709 | 68669 | 8169072.43 | 394939254.8163

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 15 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 713.3333 | 20 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 638.1783 | 13.3 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 9.75 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 272.565 | 24.3 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2758.3066 | 28.3 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 64.05 | 21 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3046.6666 | 200 | 1 | 1 | 0026-Dust suppression system | D1-Forced - Immediate | 100-Fossil-Steam
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3381.7999 | 222 | 1 | 1 | 0026-Dust suppression system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.6 | 134.4 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1937.25 | 315 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.5 | 170 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5541.9165 | 365 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.5 | 90 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182 | 91 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 896.1665 | 283 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.5 | 290 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 715.9164 | 355 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2316.25 | 272.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.15 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 651.25 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 972.918 | 139.32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1255.4666 | 64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1256.25 | 335 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2392.6664 | 388 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5836.7831 | 341 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8558.3332 | 325 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.3333 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 347.6666 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2807.25 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 272.65 | 133 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300.9 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1711.4999 | 315 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2282.4998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2981.2 | 232 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3312 | 72 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3558.4 | 278 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41648.5331 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 14.4666 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 6.6667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 63.9833 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 199.4666 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1368.75 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 746.1664 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3908.833 | 470 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 315 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.95 | 8.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 428.75 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2437.4665 | 181 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2765.1665 | 353 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 221.8332 | 242 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 834.2 | 172 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1357.4333 | 193 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1397.1664 | 830 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2274 | 379 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2340 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2412.3 | 224.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3139.0833 | 139 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3885 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4558.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12677.8331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115.9 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 312.6999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 397.4998 | 450 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 715 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 931.545 | 38.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2058.4999 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2277.6 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3281.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3548.2 | 226 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5302 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7097.183 | 479 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 702.9 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1810.8905 | 196.48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 243.8333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2801.512 | 368.62 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1264.4999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1520 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 883.65 | 137 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7153.2498 | 465 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15996.9997 | 510 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 34.85 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7624.05 | 411 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21122.5 | 595 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24604.125 | 97.5 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.35 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300.6666 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 669.6665 | 196 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 841.5 | 510 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2226.1664 | 361 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.8333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.6666 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 208.6 | 149 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 295.75 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.3333 | 82 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 912.5 | 73 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.7 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.6333 | 121 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 213.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 335.6665 | 380 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1811.8665 | 214 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2905.8331 | 317 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3327.7497 | 405 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5258.8665 | 413 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 66.65 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 244.5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 85.1 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2752.7999 | 266.4 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.9167 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.3333 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4171 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6337.5 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.6667 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 610.7 | 197 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 705.7333 | 67 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1728.3331 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1940 | 388 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2818.9333 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4196.1497 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.2 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.2667 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 363.75 | 97 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 373.5 | 249 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 431.2 | 98 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 809.0833 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1344.3332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2463.9 | 382 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4091.3 | 326 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116.6667 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.8 | 289 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1942.85 | 427 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8292.0998 | 303 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9859.4165 | 479 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 12493.9165 | 479 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 31 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 44.1667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.05 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9165 | 187 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 678.3333 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1089.715 | 198.13 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 907.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 990 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7531.1662 | 730 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25835.4 | 558 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2917.6 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.8166 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.2166 | 49 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.8666 | 112 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 262.5 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 384.4666 | 73 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 482.9999 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 548 | 137 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1969.9972 | 210.32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.75 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.75 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3016.7 | 622 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3107.8331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4350 | 500 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5874.75 | 315 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.5 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 510.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 702.1506 | 345.32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 731.25 | 325 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1954.8332 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2085 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2653.5 | 87 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3197.1332 | 403 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 18220.6 | 466 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38445.6 | 386 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 20.1 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 54.25 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4166.7877 | 386.41 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 697.41 | 309.96 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3105.4281 | 329.78 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4391.3332 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.75 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 984.9333 | 166 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 527.6499 | 183 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111398.6663 | 580 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 159.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.5666 | 83 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 337.5 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 495 | 180 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520.2 | 153 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 824.9519 | 167.22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 912.9998 | 498 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1329.8999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1583.5999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2139.8331 | 347 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4290 | 330 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6630 | 510 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7857.3328 | 830 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8745 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.3333 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.6666 | 97 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.2 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.3333 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 504 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 843.9998 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2017.0833 | 235 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2420.333 | 530 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2746.6664 | 800 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3859.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6726 | 380 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 79.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 199.3333 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 302.1 | 114 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 323.3666 | 109 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 853.8332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 47.5333 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2470.0107 | 278.05 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1249.9165 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3938.3333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.3 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.8331 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420.4666 | 212 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1499.7399 | 224.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2310 | 330 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2940 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.9333 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1170 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3125 | 500 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4202.8 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7161 | 310 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11137.5 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13684.9999 | 420 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 328.6666 | 116 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 550 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1633.3331 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1800.5164 | 427 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2000.8331 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3478.0664 | 406 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 365.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 466.3983 | 114.22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 963.0666 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1777.7559 | 239.16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 23.0667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 9.1667 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 806.6666 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6806.3332 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1330.9999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1277.5 | 365 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 736.0831 | 365 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.9 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.6667 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.0167 | 24.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 146.25 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 548.7999 | 96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 570.3332 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 804.9166 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 908.95 | 371 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1101.6 | 272 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1334 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1695.8332 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1768 | 136 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2356.6665 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.6 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.15 | 69 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 266 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 269.5 | 154 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 365 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6666 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1357.9 | 367 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1613.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1643 | 310 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2600 | 800 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.015 | 11.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 238.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 664 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 810 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 929.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1275 | 425 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1605.7998 | 372 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1650 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1684.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5033.8664 | 439 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 11688.8332 | 466 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 880.6 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 52.7 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 922.2498 | 465 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 720.9999 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 674.3333 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12974.5 | 770 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 792.2 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 62.5 | 12.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 203.3333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 9 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 408.3333 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3156.4665 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 16328.4331 | 769 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1265.4 | 444 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 4330.6664 | 448 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 1781 | 548 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 94634.1 | 711 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 5403.6663 | 559 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 288.3423 | 87.82 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.88 | 75.66 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 404.9955 | 89.01 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 708.7633 | 117.8 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2752.1699 | 165.96 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D2-Forced - Delayed | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.9999 | 168 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.51 | 59.7 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1540.0951 | 126.41 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.9975 | 41.05 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1566.3373 | 109.79 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.0548 | 43.99 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182.7676 | 148.19 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 853.6666 | 197 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D2-Forced - Delayed | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 12.8 | 3.2 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D2-Forced - Delayed | 650-Fluidized Bed
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1654.02 | 122.52 | 1 | 1 | 0040-Coal elevators | D2-Forced - Delayed | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.6667 | 8 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1848 | 84 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 743.7 | 222 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.2 | 48 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1445 | 170 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1688 | 422 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.75 | 25 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.5 | 26 | 2 | 2 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.6666 | 80 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4667 | 26 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1595.1666 | 170 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 410.05 | 139 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 468.7 | 218 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 283.6166 | 119 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240.3333 | 70 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.3333 | 38 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.8667 | 2 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1680 | 420 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2742.75 | 159 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 140 | 100 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1.25 | 3 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 552 | 184 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6735.6665 | 220 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.6792 | 12.25 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.8167 | 29 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414 | 36 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 460.8333 | 175 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1303.9999 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 329 | 60 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 681.3333 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189.4666 | 56 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 238 | 119 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 86.25 | 75 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 79.3333 | 70 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1095.25 | 337 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 443.3333 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 583.9999 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 619.8 | 36 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2193 | 170 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.6666 | 100 | 1 | 1 | 0075-Storage silos/hoppers | D3-Forced - Postponed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 296236.3332 | 340 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.5 | 30 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.8 | 12 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1326 | 340 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99 | 66 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 607.9999 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.75 | 95 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 693 | 330 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78 | 26 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.9999 | 84 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.1667 | 35 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168 | 21 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 497 | 60 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 801.8332 | 170 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 24 | 30 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 84.7 | 33 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 113.0667 | 16 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 13 | 13 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 93.9333 | 4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 51 | 17 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 0.9 | 2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2862.3832 | 143 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 8 | 2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 254.9167 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 92.5 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 138.9833 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2.75 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 14.25 | 19 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 49.5 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 154 | 28 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 120 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223.9999 | 120 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 687 | 458 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1741.4499 | 87 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.6665 | 220 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 195.3 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 105.4 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D3-Forced - Postponed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 17.8 | 3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 97.65 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 0.66666 | 4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 20.5333 | 16 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 56.1 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 696.6665 | 220 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 3.1 | 3.1 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 96 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 176 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 705 | 470 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 270 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 3045 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 423 | 47 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 5700 | 190 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 313 | 31.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7114.2 | 33.4 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171 | 57 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9075.6667 | 38 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1020 | 34 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 55 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 705 | 47 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1457 | 47 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52 | 104 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 10 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.44 | 26.1 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23 | 11.5 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.75 | 33 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.2666 | 86 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135 | 150 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 729.9999 | 300 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.6666 | 200 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.25 | 43 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.3333 | 50 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 456.5 | 110 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.7359 | 282.63 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.8333 | 110 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 792.65 | 191 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 80 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1627.4665 | 359 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285 | 114 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.8333 | 70 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13391.1161 | 309.86 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.7333 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 537.5 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 7.6 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 104.3666 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 4 | 4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510.2666 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665.7833 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.85 | 57 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.3 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 572.8333 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.3333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.05 | 79 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 956.75 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1633.3332 | 280 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 348.5 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.01 | 25.67 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1257.75 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 430 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.8 | 144 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 639 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.6666 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.4 | 46.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117.3333 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339.9998 | 240 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2232.5 | 190 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 79.1666 | 95 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 528.1833 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.2 | 68 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.2 | 46.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 393.75 | 105 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2362.5 | 350 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3052.6665 | 380 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1056.3 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 817 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1469.4166 | 55 | 1 | 1 | 0095-Bunker flow problems | U3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 11 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200.25 | 15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2093.3333 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.8333 | 41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1290 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1356.6665 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2239.9999 | 240 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2722.5 | 330 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4785 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 28.4 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 766.8333 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 824.1666 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.6333 | 13 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.8666 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.4333 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1453.4999 | 270 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 67.1 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.75 | 15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3342.25 | 461 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4518.81 | 122.13 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.5333 | 49 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 363.4 | 158 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.1666 | 130 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 494.5 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1211.1666 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 58.5 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 15.8667 | 17 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 331.65 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 39.9 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 350 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 580.5 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.8333 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 821.7 | 198 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1354.5 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 60 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23204.0832 | 307 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 473 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1322.25 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 21 | 10.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 25 | 12.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 121.1 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 94.35 | 15.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 118.35 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.825 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 456.7667 | 19.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 57.05 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 77.85 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 248.6 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 640.1 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 82.82 | 12.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 85.2 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 521.1 | 19.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 109.55 | 31.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 131.85 | 29.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 134.475 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 313 | 31.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1065 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 109.725 | 13.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 104.7617 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 130.4 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 146.9 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 124.6783 | 31.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1426.745 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 90.525 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 124.3 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 130.0833 | 22.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45.2 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 89.65 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 395.5 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 619.1283 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 3412.2 | 36.3 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 892.8617 | 20.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 48.825 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 301.55 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 326 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1650.325 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 646 | 170 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 78 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266 | 57 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.8 | 21.7 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 159.8 | 79.9 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 650-Fluidized Bed
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 15 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2900.16 | 43.2 | 1 | 1 | 0105-Bunker structures | D2-Forced - Delayed | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 10 | 20 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 17.3333 | 40 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1438.3 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 621.3 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 41.8 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 456.95 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 223.25 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.5833 | 37 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 306.2499 | 105 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 9.75 | 13 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12586.6664 | 472 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1175.2666 | 68 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 371 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 780 | 520 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1085 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3900 | 400 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 351.3333 | 124 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178.5 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2987.76 | 497.96 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12765.5 | 422 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1320 | 400 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 45 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 409.002 | 123.94 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 463.4998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 495 | 220 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2981.76 | 496.96 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.5333 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1131.9 | 343 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1575.6 | 72 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.6765 | 11.27 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 448 | 28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.4 | 88 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 127 | 127 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1528.1666 | 173 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2351.25 | 495 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.35 | 62.9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5481 | 522 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.55 | 33 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3713 | 47 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.0833 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 699.9999 | 150 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.058 | 5.18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 2 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 520 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 961 | 93 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 8.8833 | 13 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1149.84 | 15.97 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.0001 | 111.43 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 361.05 | 87 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.3333 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 899.9999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2970 | 150 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4862.9328 | 752 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.5833 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3059.76 | 509.96 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4520.8332 | 310 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.9644 | 94.77 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 183.3333 | 88 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1352.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 871.25 | 85 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 602.9832 | 143 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 26.1 | 58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 33.8333 | 58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 30.6 | 10.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 96.8 | 24.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 5.2 | 5.2 | 1 | 2 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 18.4 | 9.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 39.4667 | 3.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 7154.0831 | 293 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 387.5533 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 16.4 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 18112.2831 | 293 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 8.2 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 40.4 | 20.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 7.2 | 7.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 259.44 | 9.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5772.1 | 293 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 361.9733 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 240.9 | 73 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 28.5 | 14.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 42.4 | 21.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 141.3866 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 754 | 39 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5.2 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.2 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 20.4 | 10.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 227.1666 | 58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 14.2 | 14.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 2148.6666 | 293 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 196.5333 | 35.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.9667 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 54.6 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 66 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.0333 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 8.4 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 14 | 28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 64.2 | 36 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 9.5 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 32.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.75 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 144.7666 | 43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 3 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 33.3333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2.5667 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 43.75 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.25 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 25.7833 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 4 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 8.2167 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 42.1667 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.1 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 8.2333 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 15.3333 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.4 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 41.8167 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 60.4166 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 10.1333 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 127.9167 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2.3833 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.0667 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 120.4167 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 5.3833 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 107.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | SERC | Winter | 3725.7 | 66 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3.9 | 13 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4.2 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6.3 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 13.5667 | 22 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 5.7 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 255.4167 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 100 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | SERC | Summer | 15869.7 | 66 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 22.88 | 35.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | U2-Forced - Delayed | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | SERC | Summer | 102.8167 | 19.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | U1-Forced - Immediate | 800-Miscellaneous
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 756.6 | 37.83 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 88 | 32 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 36.5 | 73 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 29.4 | 63 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 0.192 | 0.64 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 46.2 | 22 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.76667 | 1 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 11.0667 | 2 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 27.3333 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 256.975 | 9.5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 36.1333 | 8 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 21.2333 | 13 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 268.8 | 32 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 219 | 60 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 27 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2.1167 | 1 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 45.0667 | 16 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.83333 | 1 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 24.5 | 3 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 18.6333 | 13 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 9.2 | 8 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 22.75 | 65 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.2 | 4 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 47.3667 | 14 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 74.1 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 67.2 | 63 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 88.6666 | 70 | 1 | 2 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 3518.6 | 73 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 116 | 29 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D3-Forced - Postponed | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 117.65 | 13 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 35 | 15 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 113.85 | 11 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 193.2 | 63 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 51.5 | 30 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 11.7 | 13 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 71.7833 | 73 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 55.6 | 12 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 75.1333 | 28 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 368 | 32 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 40.04 | 10.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 3369.5 | 293 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 38.85 | 12.95 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 45.8333 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 355 | 10 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 2.33 | 2.33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 6.48 | 6.48 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 419.9 | 22.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 3.0188 | 3.07 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 42.44 | 10.61 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 3.65 | 3.65 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 227.5166 | 73 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 14.98 | 14.98 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 15.78 | 7.89 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 973.3333 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 404.845 | 30.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 97.8983 | 15.1 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Summer | 420 | 18 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 812.9 | 66 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 179.3166 | 53 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 766.7332 | 212 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65 | 60 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80.3833 | 53 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 453.4833 | 169 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105.1166 | 53 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.2 | 72 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 773.9999 | 108 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 604.0666 | 68 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.15 | 43 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 963.3333 | 68 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3415.8666 | 68 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 582 | 194 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7459.6 | 68 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183.3333 | 88 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.2 | 68 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.9166 | 167 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402 | 67 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1736.4166 | 67 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2727.8498 | 267 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589.5999 | 201 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 651.1999 | 222 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 693.35 | 49 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 21.1833 | 41 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.4666 | 31 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.9833 | 17 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2026.75 | 67 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4942.9666 | 257 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8490.9 | 166 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24570 | 117 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 588.4999 | 330 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.4166 | 127 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 315.4667 | 16 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3217.5 | 117 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3831.3 | 162 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6552 | 210 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8077.7499 | 237 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 17.5 | 15 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.1666 | 142 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 599.25 | 85 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1441.3333 | 92 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15165.9 | 137 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 16 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 3 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57 | 38 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 1 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210.6 | 81 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 398.25 | 177 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 613.8333 | 127 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 793.75 | 127 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1854.4165 | 187 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1869.6666 | 142 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.45 | 7 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1858.9666 | 257 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4820.8 | 262 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.3333 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18171.9163 | 499 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.1666 | 257 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423.3333 | 127 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1150.5 | 177 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2893.1833 | 43 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1868.4999 | 222 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2396.2166 | 329 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 10 | 12 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 14 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.2 | 81 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123 | 60 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 734 | 367 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1187.0833 | 77 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1370.7165 | 217 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2224.2999 | 177 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5446.8 | 267 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22464 | 117 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.3333 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.75 | 25 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 35 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1008 | 56 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1442.6666 | 40 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 448.5 | 46 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 3106.6666 | 80 | 2 | 2 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 88.55 | 77 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 195.25 | 71 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 34.6667 | 26 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0155 | Sorbent feed pneumatic transport system including piping and valves | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1080 | 90 | 1 | 1 | 0155-Sorbent feed pneumatic transport system including piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 448.1283 | 37.87 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 910.8333 | 50 | 1 | 1 | 0160-Bed material tanks/hoppers | U1-Forced - Immediate | 650-Fluidized Bed
0162 | Bed material conveyors A | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 975 | 50 | 1 | 1 | 0162-Bed material conveyors A | U1-Forced - Immediate | 650-Fluidized Bed
0162 | Bed material conveyors A | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 84 | 14 | 1 | 1 | 0162-Bed material conveyors A | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 198 | 18 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 173 | 15 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 162 | 18 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 108.7333 | 14 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 612 | 9 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 173.3333 | 20 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.0333 | 118 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.5833 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15463 | 94 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 352.6666 | 92 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.3333 | 10 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 403.4666 | 136 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 611 | 94 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145 | 100 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 169.5999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6320 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 305.6 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 842.3333 | 95 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 806.4 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4801.5999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4860 | 120 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15933.0833 | 95 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1843.75 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.0833 | 95 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.9166 | 115 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 433.5999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16376 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185.4167 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 408.5 | 86 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 793.5999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1105.8 | 36 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8166 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2971.9166 | 95 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 538.5 | 90 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 338.3333 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 479.6138 | 92.53 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.3666 | 71 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7473 | 60 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 223.8666 | 73 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.6666 | 140 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0210 | Pulverizer heater (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 716 | 80 | 1 | 1 | 0210-Pulverizer heater (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134.3333 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.8333 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.3333 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2788.8079 | 227.04 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.6666 | 124 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 26 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 744.9 | 45.84 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.5 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.4999 | 165 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 227.5 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.5 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 978.84 | 27.19 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.5833 | 5 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223.6665 | 220 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 392.6933 | 118.4 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13237 | 155 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 388.5 | 6 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 810.0333 | 51.16 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217 | 93 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.9467 | 34.4 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15279.1666 | 95 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.3733 | 64.4 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.5 | 45 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1364 | 341 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 353.3375 | 61.45 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.1166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15.2832 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.0203 | 130.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 37.45 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.0833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.6 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.3331 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.0833 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.9833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.1833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 118.4166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 122.5085 | 27.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 199.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.75 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 330.6666 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 356.25 | 285 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 369.2 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 395.5833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 413.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 433.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 452.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 492 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 502.5833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 583.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 612 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 641.0833 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 645.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1002.3333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1186.9806 | 340.76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1394.25 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2075.1466 | 116.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2153.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2452 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4597.5933 | 71.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5688 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.2833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.9916 | 34.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.1 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.901 | 33.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.1999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.8166 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.85 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.2 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.75 | 29.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.6665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.1333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.65 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 205.3333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210.6333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 242.0053 | 113.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 303.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 341.4765 | 305.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 464.4 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 550.2499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 566.6666 | 100 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 646 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 651.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 812.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 899.6166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 943.95 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 994.25 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1152.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1249.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1587.1998 | 372 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1763.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1809.89 | 312.05 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3198 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4886.4665 | 259 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5831 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.2007 | 25.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45.1665 | 271 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 69.3333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.5 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.7333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.7973 | 75.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.7686 | 112.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 117 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120.3999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.7832 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.4 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 257.8333 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 264 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 319.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 323.8332 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 336.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 353.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 360 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 670.7833 | 241 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 832.3333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 850.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 882.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 897.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1186.65 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1972.3331 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1974.1666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2518.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2620.6999 | 219 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7222 | 314 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 28.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.4333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.5166 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 174 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 310.9667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 459.2818 | 118.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.7333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.0666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.9167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.4 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31.85 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.1999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 108.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 324.7 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 525 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.2 | 6.42 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.9512 | 133.79 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130 | 13 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.96 | 16.37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 165.85 | 93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 312.858 | 103.14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.1 | 15.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 107.35 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6600 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.8332 | 325 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 690.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 102.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 886.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 918 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79 | 79 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288.8982 | 178.7 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.0917 | 13.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.9 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.0666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.6 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 35.5666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.24 | 26.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.0316 | 91.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.2 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.8 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.6667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.6 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107.25 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.8333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 160.4166 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.75 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 174.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 183.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.9333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.55 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245.3333 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 275.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 329.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 364 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.6 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 390.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.6 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 412.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 466.6665 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 495.7999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 539.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 564.2 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 580.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 683.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 719.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 779.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 798.0333 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 825 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 913.2499 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1595 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1700.6 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1760.991 | 113.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2336.5332 | 337 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2502.4999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2974.9998 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3080.8666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4620 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7440 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.52 | 14.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.7333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.149 | 38.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.9 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.2466 | 26.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.16 | 20.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.4266 | 60.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.3166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.2333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.2333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.4166 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.9999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.1333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.5333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.3333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.4333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.3733 | 161.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 205.3604 | 155.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230.5332 | 182 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280.8 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 289.25 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 311.6 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 332.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 337.05 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 403.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 440 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 490 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 541.3333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 597.0166 | 317 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 664 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 756.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 805.5866 | 77.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 909.9166 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1007.0999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1019.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1113.9 | 237 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1120 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5856 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10176 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.2 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.6 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.0666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.9167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56.1715 | 102.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 66.4858 | 72.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.5 | 221 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136.7999 | 216 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 195 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216.4891 | 114.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 227.1666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 243.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 279.9333 | 247 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 302.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 303.45 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 361.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413.3333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 460 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 494.6126 | 81.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 588.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 600.6333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 625.4998 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 712.4 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 725 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 734.7199 | 215.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 807.4999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 829.2693 | 55.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 941.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 994.5 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1022.6666 | 236 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1260 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1279.2 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1534.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1875 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3189.9 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3491.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4505 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9882.8332 | 430 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10290 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10337.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.5333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.6666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.0667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.0833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.6333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.9166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 129 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 129.8333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 263.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 339.7521 | 77.51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 646 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.6666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.8666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.4 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.9 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 93.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.9 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104.2333 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 125.8666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 130.3333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.3 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 309.1666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 313.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1433.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1934.3 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64 | 20 | 2 | 3 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.7083 | 23.35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92 | 9.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 536.795 | 153.37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.7 | 17.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.8 | 7.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.6166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.16 | 4.04 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.5833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 339.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 755 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1113.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 522.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 831.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1482.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27905.5 | 670 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 253.2333 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.35 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.9092 | 22.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.1 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.25 | 23.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.5999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.9166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 125.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.9999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.6666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 174 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 286 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 322.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 373.3333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 403.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 603.7498 | 315 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 647.8666 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 678.5 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 695 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 726.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 774.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1183.6666 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1456.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1635.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2173.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3546 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11103.4999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14547.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.2 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 60 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.8 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.9332 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.6223 | 19.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.8666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.55 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.1664 | 325 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.08 | 23.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.2499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.8 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.5 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.65 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.1666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.6516 | 117.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.5 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.3 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 188.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.8333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 240.2666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 259.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 294 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.9841 | 155.47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 345.4333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.9 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360.6333 | 34.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 380 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391.5 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 425.3849 | 186.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 492.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 519.65 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 536.8999 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 545.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 635.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 689.0666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 810 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 830.8 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1003.8166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1066.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1235.0666 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1480 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1785 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2002 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2609.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12226.69 | 121.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.4333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.5833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.6666 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.4166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.25 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.4999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 96.6916 | 141.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 99.1554 | 97.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.25 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 157.85 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.3 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 212.75 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.3543 | 88.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230.2667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 270 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 279.9999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 295 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 363 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 426 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 513.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 592.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 712 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 718.3165 | 112.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 807.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 894.8333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 930 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1171.8666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1225.4332 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1376.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2192 | 274 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4739 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7221.3051 | 325.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106056 | 491 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.45 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.2 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 73.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 252.1333 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 388.7 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 699.72 | 58.31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2146.8 | 107.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.9333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.9 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 166.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.7 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.9166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.55 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 122.2 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 331.7 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 407.0666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1211.1166 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1471.3999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1570.8 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.95 | 14.33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1216.326 | 111.08 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.6 | 2.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 726.75 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.8 | 26.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 229.9166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 294.8 | 5.36 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.2499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.5 | 265 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 530.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 127.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 495.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 822.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 988.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 307.0666 | 49 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.2333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.3667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.7499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.5333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.1665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.45 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 53.6415 | 97.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 55.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74.0666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 80.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.5 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.7 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.3333 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136 | 272 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 159.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 160.4166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.0333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.7 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.2332 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 217.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 242.2783 | 50.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 245 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 253 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 258.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 275 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 313.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.3332 | 400 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335.75 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 485 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 491.4866 | 139.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 529.2667 | 46.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 541.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 553.2666 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 560 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 568.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 571.425 | 120.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 633.7499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 884.4 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 899 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 923.3499 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 968.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 975 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1156 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1428 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1618.5 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1856.25 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7650 | 375 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.2167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.4666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 16.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.6666 | 56 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.5667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.6667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.1665 | 259 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.5933 | 26.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.3333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.725 | 49.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.6666 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.4 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.6 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 230.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244.5499 | 219 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 294 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 299.0849 | 141.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 313.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 320.8449 | 216.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 338.85 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 395.5166 | 49.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 425.646 | 57.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 473 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 479.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 609.4166 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 636 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 723.0667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 753.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 775 | 310 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 961.8343 | 308.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1085.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1268 | 317 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2053.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2625.5 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.6 | 18.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.05 | 12.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.4333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.3333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.6333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.6 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.0167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.2666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.9167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.8665 | 208 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.6 | 353 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.7567 | 39.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 77 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.3667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 122.5 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 168.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 203.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 216 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 318.4999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 347 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 468.1666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 484.2 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 524.25 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 624.69 | 59.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1057.4 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1334 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4903.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.8667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.1 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.65 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 209.25 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 250.4833 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 277.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 1208.7532 | 342.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.3333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.4 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.4 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 193.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 360.9166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.15 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.2167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.3 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.4833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 112.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 190.1333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 237.3 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.28 | 14.32 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74 | 3.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.476 | 2.37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 808.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.04 | 2.48 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.95 | 5.15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 2.75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.2666 | 152 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.08 | 13.52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 468.02 | 66.86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 473.6666 | 203 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 580.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.5832 | 215 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1030.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 277.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 373.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 498.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 528.2 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 936 | 135 | 1 | 2 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2608 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 80 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.675 | 34.9 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 770 | 140 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2250 | 250 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.9166 | 335 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.1 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.8333 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.1667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.2333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.04 | 156.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.6666 | 80 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.7 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68.1999 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.5333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155.7333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157.2 | 262 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 164.8499 | 141.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 168.2 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.8033 | 128.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 235.8666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.7166 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 290.4 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 318 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 376.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 504 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 677.7331 | 299 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 748.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 789.8991 | 125.05 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 898.3846 | 132.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 998.25 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 999.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1165.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1320 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1353.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1416.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1690.616 | 272.68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1929.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2772.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4849.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5715.1665 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.0833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.9333 | 26.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.15 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.7499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.2666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.8332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.4999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.5333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.1499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.6666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.3 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.0693 | 49.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 196 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.5 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.125 | 55.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.3333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.7 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.4 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.0666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.7666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.4733 | 161.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.1166 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125.0333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.835 | 93.89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.1 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.0165 | 247 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.6 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237.3 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 274.2666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 295 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 326.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.3149 | 216.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 376.8254 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 421.9166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 465.75 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 493.9333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 499.5 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 502.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 528 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 614.68 | 30.48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 633.0832 | 355 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.6166 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 651.6 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 708.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 738.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 761 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 804.65 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 863.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 950 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1351.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1507.8333 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2008.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3480.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3615 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5487.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.1 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.7083 | 30.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.05 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73.2 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125.7666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150.2666 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160.9999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 259.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 261.9997 | 393 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 305.2 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 355 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.6 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 405.1833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 479.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 534.2999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 583.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1190.6665 | 380 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1314.8332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1467.008 | 114.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1475.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1642.5 | 450 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2157.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3474.4165 | 241 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6386.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 10.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.6 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.0166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 182.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 305.5666 | 206 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 326.4 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 342.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 2475.9932 | 312.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.0167 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.4167 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.6333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.15 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.6 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.3 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.25 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.4 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 166.2666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 251.1 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 352.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.7 | 8.45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.4 | 7.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94 | 18.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.4 | 8.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.7333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.4 | 5.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 664.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 727.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1236.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 283.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 223.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78199.8328 | 830 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.2665 | 232 | 1 | 1 | 0250-Pulverizer feeders | U2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.95 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 11.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 28.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.5 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.8 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.7 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.4333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.2666 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134.9 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 178.3333 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192.4999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 219.5333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 233.6166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 275 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 343.2 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 361.0999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 389.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 550.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 576 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 670 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 869.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 906.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 939.4666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1183.4666 | 126.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1299.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1683.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2228.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2483.2 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5275.6 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.45 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.4333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.9 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2266 | 26.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.5333 | 66.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.8333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.1999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.1333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.25 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.675 | 19.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.8666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.8 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.4666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 119.6266 | 44.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 122.4166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.2833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.0833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.3833 | 27.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.25 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.3333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 252.8166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 309.91 | 36.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 347.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 377.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 411.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 540.75 | 216.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 602.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 720.7999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 730.05 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 770.8333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 803.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 884.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1120.0666 | 212 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2056.5666 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.2665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.5499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.85 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35.5666 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.65 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.4 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.792 | 51.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 97.3331 | 365 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.018 | 240.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 114.3613 | 122.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 306 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.2 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.9999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 203 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 263.3368 | 115.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 422.9166 | 203 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 452.8333 | 247 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 584.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 609 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 648.822 | 127.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 728.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 761.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 876 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 933.3332 | 400 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1038.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1219.3999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1221.9166 | 341 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1639.995 | 156.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1993.3332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2482.272 | 365.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2517.1999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2734.7 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3822.9332 | 256 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.3 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.55 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.4167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.0666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.1 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1150.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1292.6 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.1333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.2666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.0333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.8166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.4666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 46.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.9833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.1833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1489.5282 | 158.18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.8677 | 18.73 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.88 | 2.88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.98 | 32.33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.8 | 10.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3051.2724 | 123.45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.2 | 10.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1316.1 | 123 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.8333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.0832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 876 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1340.7 | 82 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1732.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.2 | 17 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 324.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 131.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1770.7499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.3399 | 114.3 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 247.45 | 21 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.25 | 111 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 483.3333 | 116 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.0333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.9667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.3333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.0353 | 38.23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.9038 | 42.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.3333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.4 | 126.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.698 | 75.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 108.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.9333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.1333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 127.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 130.1666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136.7999 | 216 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.9 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.6 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 191.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 206.25 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 236.25 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249.4166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 261.197 | 17.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 386.9435 | 29.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 541.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 644.8 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 656.3666 | 203 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 664.5 | 443 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 777 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 791.715 | 112.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 855.1332 | 254 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1155 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1380 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1470 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1519.4666 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1713.25 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2146.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2199.98 | 126.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2560.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2636.71 | 44.69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2667.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2766.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.45 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.3 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.9852 | 18.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 22.2479 | 83.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.8416 | 39.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.0499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.6399 | 75.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.0832 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.8666 | 161.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.8333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.4999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.9333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.6333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.4999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.755 | 26.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266.4 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327 | 218 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 401.85 | 107.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 405.5999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 431.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 452.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 453.25 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 517.9999 | 222 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 573.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715.5 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 765 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 986.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1776.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2099.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2160 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.5666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.202 | 14.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39.8666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.368 | 85.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.2499 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.8166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.9666 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.7 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 127.3999 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 152.5332 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.6833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240.1279 | 215.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 283.1999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 293 | 73.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 303.3333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 328.3499 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 385.0545 | 111.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 462 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 494 | 247 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 497.9333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 655.75 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 800 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 924.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1173.3332 | 256 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1872 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2214.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2433.5359 | 215.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2746.6666 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3789.8666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6160 | 385 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6356.7098 | 290.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.9333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.6 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.6 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 95 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 420.2666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 644.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 694.7333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 970.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30.0667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.65 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.1166 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 155.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 174.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 409.0666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1919.9499 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1815 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 16.2 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1588.02 | 13.93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 398.35 | 93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1100 | 88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.5333 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.2 | 17.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.87 | 4.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.8833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1024.8 | 21.35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1334.16 | 12.24 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1419 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 259.9 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 318.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 553 | 79 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 837.2 | 299 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6124.4 | 502 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1683 | 39.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.4666 | 44.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.0166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18.5 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.8833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.2667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.4 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 109.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 117.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 146.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.7333 | 122.24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.8833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 221.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234.0333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.1716 | 58.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.7 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 359.6805 | 67.23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 362.85 | 177 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 390.0833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 403.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 406 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 440 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 441 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 526.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 604.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 658 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 705 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 717.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 833.9799 | 135.24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 858 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 881.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 905.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1013.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1062.32 | 65.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1225.1283 | 84.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1322.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1535.7251 | 286.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1670.347 | 138.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1803.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1864.2135 | 83.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2046.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2111.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2641.4666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3241.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4910.4 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.1833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.9333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.2999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.4 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.0166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.23 | 47.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.4833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.35 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.7 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.8 | 76.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.8333 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207.2 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225.8666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 301.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 309.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 320.5999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 372.6165 | 283 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 381.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 465.8333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 601.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 808.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1138.25 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1631.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2605 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3485.5832 | 277 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12846.1665 | 605 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.73333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.5167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.5 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.9507 | 46.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21.35 | 91.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.4333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.3333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56.1 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.8 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.25 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 96 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.384 | 33.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 118.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126.85 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.5998 | 348 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.05 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155.5 | 311 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 199.624 | 249.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 217.1498 | 303 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 238.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 264.096 | 82.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.9999 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310.0166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.2142 | 138.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 488.4 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 575.75 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 594 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 597.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 708.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 746.823 | 66.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 777.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 850.9999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 893.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 957.6 | 252 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1058.1999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1075.2733 | 124.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1340.45 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1848 | 231 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1932 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2009 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3132.2499 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12056 | 274 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.1833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.4166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.3 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.8667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.05 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.4 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.1333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 176.2166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 230.4 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 550.55 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 562.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2805.84 | 116.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.4 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.6 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.4166 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.1333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57.9666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.1333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.3 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105.75 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 210.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.06 | 212.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 219.0167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 482.4 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1084 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 3.6 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.68 | 14.67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1532.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66 | 3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100.75 | 13 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.6 | 3.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.5 | 13.25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.3666 | 163 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 306.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.029 | 242.37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.5 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104.2666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.1333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 210 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 305 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2002.0832 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 136 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 172.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 242.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 347.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198 | 33 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 266 | 38 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1586 | 610 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 171.9 | 382 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4545.15 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 103.9167 | 14.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 154.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 883.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 834 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 70 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 53771.8 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2133.3328 | 800 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 417.0833 | 65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1139.301 | 123.39 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 471.2499 | 435 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 590.4666 | 68 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.5 | 26 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 219.7 | 13 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2374 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 481.6666 | 68 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.6833 | 29 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 154.85 | 57 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10072.9999 | 210 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.5783 | 86.15 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.5 | 41 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.3333 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.5 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.8833 | 73 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 322 | 56 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1543.6 | 68 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24791.4 | 54 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.0167 | 13 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167.1333 | 46 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 62.4999 | 150 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378.0666 | 107 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 737.9166 | 115 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.5 | 18 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 190.8333 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364.8 | 114 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1578.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.2 | 61 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1730.5833 | 95 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105.896 | 68.32 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.3093 | 39.32 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195.25 | 33 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.2 | 98 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.55 | 71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1046.4999 | 210 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 565.5 | 390 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 892.9665 | 178 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1640 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.9166 | 95 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.6333 | 56.6 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.8333 | 115 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 285.75 | 127 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7518.9997 | 876 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40967.15 | 469 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.6665 | 250 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5802.2399 | 115.2 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.9999 | 75 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.5 | 95 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.2 | 66 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 148.5 | 90 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.9999 | 120 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.835 | 36.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165 | 165 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 188.7999 | 96 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.5666 | 95.6 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.26 | 27.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.1666 | 65 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 429 | 130 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.7333 | 28 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 294.99 | 98.33 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.8332 | 125 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1067.9999 | 90 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 10 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.5 | 78 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1095 | 100 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.9999 | 123 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.9999 | 120 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 259.15 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1073.4666 | 83 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.5999 | 159 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 498.3333 | 130 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.7146 | 223.76 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195.4999 | 138 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1407.6332 | 349 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192.8833 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.2666 | 123.76 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.75 | 45 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.7474 | 88.95 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352 | 30 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.2832 | 143 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 683.9666 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 423.6665 | 410 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 159.75 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1000 | 125 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.8332 | 203 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34.8426 | 130.66 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 666.6666 | 125 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 4874.6666 | 80 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 3006.3999 | 96 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1214.5664 | 82.53 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1512.5332 | 128 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 894.5833 | 113 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D3-Forced - Postponed | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.5 | 81 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.7 | 57 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135.0153 | 130.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2655 | 108 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 988.2 | 122 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1798 | 145 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.1332 | 152 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253.3333 | 190 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 404.4165 | 211 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3621.3666 | 122 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 746.9396 | 130.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1010 | 202 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 605.843 | 170.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12542.6666 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.0666 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.5 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.5 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.2 | 24 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 287.4666 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1192.7499 | 195 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21571.8665 | 307 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 120.6667 | 36.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.2333 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 519.4 | 84 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.5 | 310 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 633.06 | 35.17 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 927.2 | 48.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1629.3419 | 170.91 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2557.728 | 38.52 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.4 | 6.97 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127 | 30 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18287.5 | 1330 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.3 | 93 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.2333 | 2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 352.6399 | 91.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450.3666 | 118 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 626.5831 | 365 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 817 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1003.5667 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3913.3333 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6512 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9084 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 20.6183 | 8.9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.0666 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.6 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.9999 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1850.5998 | 228 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3510.7333 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 680.1133 | 240.04 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 5031 | 468 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 620.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.92 | 1.47 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.25 | 281 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148 | 148 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1013.8 | 13.7 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14 | 56 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116 | 80 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 405.363 | 6.79 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1892.3333 | 28 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 333.3333 | 100 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45140.6664 | 680 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.0999 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.3166 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183 | 122 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 869.1999 | 123 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 940.0833 | 145 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5440.4 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11082.5 | 310 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11520 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15026.8666 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.3333 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 91.64 | 69.6 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 531.6499 | 93 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2406.3333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2800 | 350 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.4667 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21340 | 485 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1409.9998 | 225 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 4.05 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.1 | 3.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460 | 368 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 664.02 | 31.62 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1491.78 | 21.62 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.3333 | 65 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 370 | 100 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 490 | 49 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.5 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.0833 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.4666 | 88 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 220 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1076.6665 | 380 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9083.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10652.4999 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.3 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566.7666 | 98 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1079.991 | 327.27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1533.5833 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2170.35 | 117 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8829.1665 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.72 | 31.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 212.6897 | 11.74 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3900 | 520 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1326.0733 | 55.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.9166 | 55 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.9997 | 465 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 59 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1969.35 | 691 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4246.6662 | 700 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12000.333 | 518 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.9167 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.1332 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 250.7266 | 105.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107894 | 365 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.8 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 460 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1261.8333 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1442.5332 | 248 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1701.7 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4715 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27373.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.9167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 422.9167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 664.7 | 28.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 196 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1950 | 100 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2159.75 | 265 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11836.6665 | 530 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 156.7999 | 168 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 478.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 784.7 | 118 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3571.4666 | 118 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.6 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.8 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.1333 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 200 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 440.75 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2470.6664 | 340 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 78 | 31.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 501 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 823.1625 | 415.04 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9522.333 | 530 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.8 | 29.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 299.49 | 4.47 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1392.2133 | 25.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 132 | 120 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.9999 | 120 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8657.1665 | 635 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 257757.5 | 770 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 758.44 | 113.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 850 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1578.1 | 367 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2640 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5041.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.4667 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 643.95 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1035.4998 | 327 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1173.3332 | 200 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5545.332 | 450.84 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.16 | 55.58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1142.3333 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.08 | 4.64 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 689.12 | 5.84 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 149.5 | 115 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 170.0283 | 28.9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.2 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 855.8329 | 650 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 930.6 | 188 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3441 | 222 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4966.1664 | 830 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.9333 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.4 | 116 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 403.3332 | 200 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 847.6333 | 118 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1166.0533 | 47.92 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.3333 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.25 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1191.6666 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2181.5497 | 483 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2733.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62 | 248 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.6667 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589.0323 | 134.38 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2103.35 | 7.13 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.5 | 70 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1151.5 | 470 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.3333 | 25 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10627.5 | 130 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3246.2498 | 525 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56703.7499 | 225 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 157.9667 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1027.1331 | 284 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.6 | 198 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.9 | 173 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72.3333 | 31 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.1999 | 102 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798.2333 | 77 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.5 | 15 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 722.5 | 425 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1425 | 95 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3050 | 305 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4587.4995 | 750 | 1 | 1 | 0263-Primary air fan drives | U2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444.6 | 117 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.1166 | 53 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5739.55 | 601 | 1 | 1 | 0263-Primary air fan drives | SF-Startup Failure | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 649.2499 | 159 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1262.5 | 505 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4680 | 160 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15383.25 | 43 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.5833 | 25 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1804.7333 | 107 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8143.3333 | 175 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.3333 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 449.2666 | 46 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58335.3329 | 635 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.3333 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.25 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 494.0833 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 164.6498 | 267 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24510 | 43 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1013.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2135 | 427 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 603 | 134 | 1 | 1 | 0263-Primary air fan drives | U2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1465.3333 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 20 | 2 | 2 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68569.4165 | 635 | 1 | 1 | 0263-Primary air fan drives | U3-Forced - Postponed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 822.5 | 75 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376.6666 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 80 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5551 | 305 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 481.6666 | 85 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6873.5499 | 417 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1045.9999 | 120 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77 | 11 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1485 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2219.9994 | 900 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 113.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 246.5833 | 11 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13417.0832 | 325 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 117.2499 | 105 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 176.9166 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 881.6666 | 230 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 97.4666 | 344 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 7039.7831 | 727 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.15 | 97 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9747 | 162.45 | 2 | 2 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.0832 | 125 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.8333 | 130 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10614.4998 | 690 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1487.5 | 170 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2212 | 84 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.2 | 102 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 203.1666 | 230 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 230 | 230 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13349.6663 | 580 | 1 | 1 | 0264-Other primary air fan problems | U2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 80 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.3333 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39 | 12 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1303.8 | 106 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1919.1665 | 350 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9128 | 28 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 537.5 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 15 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650 | 50 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 916.3333 | 20 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1000 | 500 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.0833 | 5 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 93.6666 | 281 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.5833 | 175 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77.5 | 155 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376.2 | 26.4 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1565.6497 | 519 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2265.0833 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.0016 | 114.55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 584.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 950 | 95 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1669.4498 | 579 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16516.4999 | 234 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6638.7495 | 705 | 1 | 1 | 0264-Other primary air fan problems | U3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.6666 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 894.833 | 455 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1352.9 | 163 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.24 | 26.4 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522 | 580 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 5.0333 | 2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 650-Fluidized Bed
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 28806.5575 | 89.81 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1421.0499 | 291 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7832.3665 | 521 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 557.7498 | 291 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2402.5 | 310 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24 | 80 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5264.9664 | 346 | 1 | 1 | 0265-Primary air heater | SF-Startup Failure | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.4 | 6 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10370 | 100 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21678.4 | 272 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120142.1662 | 742 | 1 | 1 | 0266-Primary air heater fouling | U1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 31.46 | 2.42 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.21 | 2.21 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.9 | 2.9 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 12.06 | 4.02 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 77.224 | 3.36 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.6 | 2.6 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.46 | 2.46 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 4.8 | 2.4 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 650-Fluidized Bed
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5172.5 | 150 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.8 | 12 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.5 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.5499 | 159 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2563.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.4166 | 25 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85.2499 | 165 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3347.833 | 530 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.1 | 43 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163.1667 | 22 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 264.45 | 123 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1121.3333 | 145 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1024.9996 | 615 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 169.5366 | 56.2 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3752 | 469 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.1666 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1873.2999 | 78 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.25 | 15 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.4 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.5833 | 5 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1121.9999 | 90 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.5333 | 41 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195 | 150 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 422.9167 | 35 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22933 | 71 | 1 | 1 | 0267-Primary air flow instrumentation | SF-Startup Failure | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.4666 | 281 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 207.9998 | 240 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 477.5 | 25 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.75 | 15 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.4 | 64 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 367 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.4999 | 150 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.5 | 5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177.6666 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 834.716 | 59.34 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 930 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 949.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4427.5831 | 335 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 605.9664 | 343 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 733.95 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 988.2666 | 272 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1000 | 200 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2191.3333 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2898.5 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.0666 | 64 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 676.3666 | 103 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1146.5333 | 8 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 687.8667 | 8 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.0639 | 172.32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 307.4999 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 401.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3774.75 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 110 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225.4 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 551 | 114 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 821.4999 | 159 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5233.3333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4709.1033 | 172.6 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.8 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1049.4 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1940 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.5 | 17 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.5666 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 297.5 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.9833 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 670 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1295.6 | 79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3946 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.5 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.9 | 22 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.9999 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 252.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 340.3816 | 155.9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 383 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1183 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2546.25 | 485 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.8333 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 531.5332 | 134 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.2499 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.3333 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 225 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.2499 | 177 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.6666 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 281.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.25 | 71 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 430 | 430 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 593.5999 | 159 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1173.3332 | 400 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6799.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15498 | 820 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185 | 74 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200.6666 | 172 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 609.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 758.3333 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.1 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 512.5 | 250 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1566.9666 | 129.68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17152.6666 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34.9999 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 507.1499 | 189 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 567.9998 | 240 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 924 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1083 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1185.3333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1468 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3077.325 | 87.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4375.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.3 | 18 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.6666 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 745.5833 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1568.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.5 | 21 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810.75 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4463.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 286.5 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1479.6666 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 177.7333 | 62 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2695.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220 | 88 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 429 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69652.9329 | 626 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6382.3331 | 820 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.6333 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.5833 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.35 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 222.5 | 178 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 250.8333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2365.9166 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.5 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 666.25 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1720.6665 | 178 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5572.0832 | 215 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 260.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.5665 | 247 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 482.9998 | 252 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 207.12 | 172.6 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3998 | 8 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12209.1665 | 650 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287 | 41 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 426.25 | 93 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 484.5 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4443.6 | 168 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.5 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.3333 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 698.3333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 781.05 | 123 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 923.1332 | 227 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44.2 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 91.1166 | 77 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1454 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.25 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 196 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21951.7329 | 626 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 10305 | 229 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 11229 | 591 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 5627 | 331 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 5336 | 116 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156 | 240 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1330 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 541.4166 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 806.6666 | 121 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2714 | 92 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.4 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290.5 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3057.6 | 196 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3519.0999 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6913.2859 | 165.72 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 180 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.75 | 103 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2011.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 11 | 11 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.3 | 121 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 888 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1936.9833 | 163 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2288.7833 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154.7 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2212.9163 | 565 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.6666 | 230 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.0628 | 86.63 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 540.8 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.4 | 2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.5999 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1415.1408 | 53.57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1483.3333 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5679.5 | 74 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4778.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.6666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 54.612 | 136.53 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 336 | 144 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7710 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8028.8331 | 335 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10909.8 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6911.6666 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.75 | 45 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 705.6 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 939.1666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20367 | 310 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 316.5 | 422 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.4999 | 210 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8272 | 47 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6188.949 | 131.82 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.2166 | 53 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.9833 | 107 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.9 | 283 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 682.5 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7678.9999 | 84 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 210 | 100 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.2166 | 127 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.9999 | 144 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 718 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 742.922 | 256.18 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1235 | 380 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1593 | 177 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3363 | 57 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2070 | 180 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2769.4333 | 77 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.4 | 63 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1056 | 88 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3226.9999 | 210 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.317 | 29.01 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.5 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 228 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.7333 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 316.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1563 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7074.3995 | 717 | 1 | 1 | 0280-Pulverizer fires | U2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 430.6152 | 266.36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1675.083 | 25.89 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7703.584 | 33.32 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.5167 | 23 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5878.57 | 25.14 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 667.3333 | 55 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1386.21 | 20.09 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1750.719 | 196.71 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126.5 | 69 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1486.4626 | 41.56 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3375.1667 | 35 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94 | 47 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1089.5832 | 125 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 251.2 | 24 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2514.08 | 33.08 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4508.4 | 312 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 555.7999 | 84 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.3333 | 23 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.96 | 127.95 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.3333 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274.0833 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 777 | 222 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2655.5833 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3198.2833 | 127 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.61 | 142.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 920 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1130.9999 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3983 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17683.75 | 101.05 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.2667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.1333 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.5 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.65 | 29 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.4667 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.0166 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.0167 | 29 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51.3333 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73.6666 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 752.6332 | 134 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4300 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6877 | 299 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 398.4666 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76.2667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1003.5666 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137216.7499 | 165 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.3332 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 148.75 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2426.6666 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.3333 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.5333 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 206.8667 | 29 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 208.8 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 234.0333 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 673.2 | 204 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2183.2 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3347.5833 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 333 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1630.5164 | 361 | 1 | 1 | 0300-Pulverizer motors and drives | SF-Startup Failure | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.4 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 737.9166 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2163 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5367.5 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.4166 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.9166 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25.6666 | 154 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.2 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.8 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119.5333 | 163 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 189.2 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.6 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 535.5 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 545.9333 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 793.0333 | 74 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 896.9333 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 109.8326 | 227.24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 750 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2494.7382 | 662.32 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 642.4 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 896.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1150.2 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1621.6666 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9845.3333 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.5 | 41 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 383.3665 | 217 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.65 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47.5 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95.0666 | 124 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 146.25 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 223.2666 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 231.3 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 388.5333 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 689.7 | 114 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 893.2 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2200 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 231.4 | 26 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 428.2061 | 122.93 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 666.6666 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1048.4833 | 77 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16455 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 557.6 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 799.1998 | 324 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 966 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1016.6666 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.45 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.5333 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115.6 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 352 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375.2 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 574.9333 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 763.4 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2128.75 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5797.9663 | 619 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.0999 | 93 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 486.6517 | 49.49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.75 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 346.5 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 475 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1139.6666 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.096 | 113.22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31.5 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.2 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.8 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 89.5999 | 84 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 129.6 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 256.25 | 205 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 354.1333 | 64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 372.8666 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2750.8 | 104 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4031 | 139 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 175.0005 | 70.47 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.3333 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 181.9166 | 59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.2666 | 37 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.5 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.4999 | 210 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8300 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.1333 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.1333 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.6 | 69 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.8667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.6 | 74 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.2333 | 98 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 101.0167 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.3333 | 184 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 169.4333 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 245 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 428.4 | 84 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 468.8 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1556.5333 | 104 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6600 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2167.6666 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 137.3175 | 183.09 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1054.083 | 455 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2973.1329 | 644 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4212.4995 | 750 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 511 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 693 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 796.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6192.5 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.3333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255.6666 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1334.4333 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1393.0167 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1571.1666 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.9333 | 16 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 122 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 126.9 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.9999 | 144 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 192.4 | 104 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 206 | 103 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 303.3 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 405.0666 | 124 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 716.95 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 791.9833 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1408.95 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3690 | 205 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12531.6 | 177 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.9999 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 286 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.95 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.6333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.45 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.15 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 251.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.5333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315.0666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 431.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 490.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 590.5833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 592.2 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 615.9998 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 641.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 712.5 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 921.156 | 158.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1368.1066 | 96.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1808.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1994 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2660 | 532 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2936.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4039.0819 | 153.48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4048.469 | 535.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4845.2332 | 274 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10258.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10548 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13595.6333 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15813.2333 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18554.9986 | 104.87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.65 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.59 | 123.18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.1533 | 49.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 103 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103 | 51.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170.6833 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 237.9666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 239.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339.1666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 389.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 395 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 452.2 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 455.1166 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 625.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670.9333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 713.5333 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 798 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 833.6665 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1280 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1335 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1358.0001 | 150.61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1619.6666 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3285.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5550 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11052.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42997.0666 | 157 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.5333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.0667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.0833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.7 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 134.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.7333 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 328.6666 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340.5831 | 335 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 464.6665 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 593.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1131.6666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1943.9785 | 535.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2434.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5903.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 224.0999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 448.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595.3333 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 363.3 | 519 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5178.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.1666 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.9 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 743.6666 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.3666 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.16 | 83.44 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316 | 80 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 231.15 | 20.1 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5414.4 | 48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7335.36 | 815.04 | 1 | 1 | 0310-Pulverizer mills | SF-Startup Failure | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 980.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.0013 | 6.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 94.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.6499 | 231 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168.1333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 509.9998 | 360 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632.6 | 316.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 715.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 809.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 912.6666 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1064.187 | 219.42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1219.8 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2028.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2391 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2408 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3633.2582 | 171.65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4572.5832 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8340.4166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17952.5 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20285.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.1333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.0666 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.9666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.5 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.7666 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.72 | 58.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.56 | 116.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162 | 40.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 281.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 372.6 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 525.5833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 529.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 530.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 741.4165 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 836.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 969.75 | 323.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1023.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1183.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1440 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1636.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1864.7072 | 160.52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2117.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2765.3333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4472.2666 | 248 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4634 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12468.8666 | 77 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12656.2449 | 317.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35938.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.9666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160.1035 | 26.61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 216 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.4166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 277.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 316.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 388.4166 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 530.4 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 701.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1130.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1608.3332 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1924.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2249.6 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2530 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3041.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6113.9999 | 360 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16325 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1.35 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.2333 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.95 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 244 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 342.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.1617 | 9.38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.8 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.7833 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.5 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 424.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.2666 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.25 | 325 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.5832 | 245 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159 | 159 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.6 | 44 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 162.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 346.9166 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1077.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2780.6664 | 860 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.85 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.6666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 172 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 214.4 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 214.8 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 245.9333 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 326.0665 | 292 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 334.1333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 405 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 494.55 | 141.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 565.2 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 711.12 | 296.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 857.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 892.1173 | 37.12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 938.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 969.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 997.8 | 166.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1090 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1171.3 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1190 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1697.5904 | 348.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2175 | 174 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2246.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5530.6666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6381 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6777.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7660.5106 | 150.01 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18658 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27281.3332 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62719.95 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 2 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.1333 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.2667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.3331 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.9167 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.5999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.3332 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 241.9999 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 317.1166 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.9 | 28.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 412.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 458.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 622.75 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.25 | 285 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 654.36 | 62.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 853.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 933.3333 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1487.0833 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2850.6333 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3868 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4244.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5316.1333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.3333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.2167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74.4 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.0999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.5126 | 59.08 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.4 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106.8833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 178.9333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 229.1666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.3298 | 61.63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 520.4833 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 533.933 | 87.53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 783.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 787.6 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 929.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1327.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1346.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1621.5 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1920.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2145.1666 | 305 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3345.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4216 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8625.0665 | 208 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9099 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17920 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32393.15 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.8 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.1 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 670.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 396.4666 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1248.9333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2544.1 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 303.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.937 | 33.31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 899 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2810.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469.6791 | 49.01 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.9 | 11.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280.08 | 46.68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 372.4166 | 109 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1585.2998 | 249 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2286.5833 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.2333 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.9166 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.75 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 594 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 610.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 635 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1534.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.1767 | 47.24 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1494 | 249 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 237 | 79 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4022.6665 | 560 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5385.2328 | 773 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.6 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.1833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.5733 | 116.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 231.8666 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 233.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234.5383 | 116.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.7499 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 309.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 396 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 474.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 512 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 535.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 558 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 686.3999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 735.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 813.1667 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 830.7333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1282 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1564.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1674.1666 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2013.9166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2175.4333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2203.563 | 114.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2354.9999 | 225 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3537.8 | 532 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3569.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3902.85 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4109.4666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4285.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4425 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5460 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5740.1099 | 124.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12868.5039 | 169.62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14519.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.8667 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.0333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.9166 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.1666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.4833 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.1666 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 223.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.5 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238.15 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 331.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 749.6666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 832 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2216.6665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2251.953 | 108.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2626.7333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2692.0833 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3024 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4893.1665 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14984.7519 | 297.12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42834 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.1 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.5 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.6664 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 161.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.8 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 179.1666 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 327.8 | 298 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.0803 | 191.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 480 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 515.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 711 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 723.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 881.3665 | 386 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1021.85 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1184.9 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1256.5833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1276.8333 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1612.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2261 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4277.9832 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11324.25 | 315 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12408 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13279.9999 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183.6666 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.0667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.7157 | 22.78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.3 | 58.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.4166 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 322.2833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 925 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 32088 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5176.5 | 8.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 2.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7163.8121 | 53.87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1574.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800.26 | 23.38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4837.4333 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.3333 | 190 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 265.4166 | 245 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 325.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1648.2 | 134 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1906.1999 | 162 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.8667 | 29 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.9166 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.5333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.2 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.3333 | 34 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.6166 | 49 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 225.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1436 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2193.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.6166 | 178.7 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.25 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90 | 180 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.6167 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 183.3475 | 104.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 285.7166 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.5833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 642.7362 | 258.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 753 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 836.3599 | 216.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 941.1999 | 156 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 963.2 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1234.212 | 167.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1240 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1345 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2278.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2289.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2620.8333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2865.9666 | 254 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2934.6666 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3034.5699 | 168.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4340 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4668.6492 | 190.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6801.4166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10710.2999 | 171 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18980.5416 | 135.98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.2 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.6667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.6666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.75 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182.25 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.3332 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 216 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 249.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 304.4274 | 125.97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 311.2399 | 233.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.6666 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.35 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 495 | 660 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 544 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 609.1664 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 701.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 737 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 778.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 953.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1234.2 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1602 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1706.8425 | 109.53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2409.96 | 114.76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4024.3666 | 125.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4148.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6120 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6533.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21228.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.55 | 10.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.3383 | 42.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.92 | 86.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 232.5 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 312.8665 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 656 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 733.3333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 738 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 947.9166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1208.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2417.8 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8500 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9715.2666 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 182.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.45 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.3333 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4265.6333 | 73 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1682.4833 | 59 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.6 | 14.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.2333 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.4 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.4667 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 416.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1140 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5173 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.1 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.05 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 158.2333 | 94 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 160 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 994.3333 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5176.4996 | 630 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11220 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.6333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.4666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.9975 | 34.05 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.4493 | 58.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.8333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.1 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126.4667 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.6 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.1498 | 50.09 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.5333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.3333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 277.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287.1333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287.4666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.6 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.6 | 166.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 372.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 417.9166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 459 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 521.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 583.9166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 625.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 654.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 930.8 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 953.9999 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 960 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1142.3332 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1252.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1970.3 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2010 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3851.5722 | 528.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5127.5832 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6399 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8175 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19613.8332 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23493.7999 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86000.0236 | 114.94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.7 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.6516 | 151.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.156 | 12.24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.6167 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34.4 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.5833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.7833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193.3266 | 49.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 227.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.6666 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 518.7333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 906.9666 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1203.3166 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1870.625 | 102.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3387.628 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3571.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3622.4998 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.8333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.26 | 216.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136.62 | 59.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 142.3331 | 305 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 175.1999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.5 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 288 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 342.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 384.9998 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 536.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 570.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 582.9998 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1035 | 460 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1226 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2173.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5802.8 | 65.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5992 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6102.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7862.8 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 202.4 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3750.9499 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12555.2 | 236 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.7333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.6833 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 130.4666 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 231.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2572.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 583 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3011.5 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.2 | 10.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 573.1666 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 625.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.3333 | 190 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1542.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1680.9665 | 422 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3166.8 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.8833 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.8166 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.5833 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 361.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 423.5 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 615 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 756.2497 | 375 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798.8666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 828.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1021.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1040.271 | 158.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1313 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1683.4102 | 528.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2412.4999 | 375 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3400.3333 | 202 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3572 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3617.6 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3931.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4800 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4843.9166 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5377.115 | 208.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10516.4997 | 405 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11853.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.75 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.65 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.3333 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 209.7666 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 210.6 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274.05 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 309.9786 | 83.03 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335.25 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 340 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 517.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 668 | 167 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 900.7916 | 166.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1090.6833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1154.9333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1199.9999 | 360 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1605.9332 | 221 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2404.65 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3653.1795 | 233.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6098.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10842 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10880 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24555.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44239.2 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51288.6999 | 354 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.9767 | 21.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.55 | 30.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47 | 47 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 48.6665 | 182.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 68.1005 | 104.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.7333 | 208 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.8666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.9333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113.1 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.0666 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.7499 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 153 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 223.3333 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248.9 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 252 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 394.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 442 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 447.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 517.0833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 525.6666 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 814.3 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 819.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 872 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1026.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1165.5 | 518 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1262.3 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2189.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5755.3333 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13754.9999 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.0333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 134.5833 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 352.1333 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 471.2 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 640.1 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13.4167 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 147.4 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 252.2166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1392.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2346.1333 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.8 | 6.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.5 | 215 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 176.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220.35 | 113 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 888.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5391.5833 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.05 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132.3 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.04 | 57.78 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 590.7166 | 67 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2055.8999 | 126 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.3333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.2333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.1 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 339.7332 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 410.6666 | 123.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 488.6333 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 507.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 571.9333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 651.105 | 310.05 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 708.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 904.05 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 924.8332 | 310 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1106.95 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1215.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1496.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1772.9166 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1884.2066 | 165.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1928.1499 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1963.8499 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2650 | 530 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2762.3076 | 145.13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2975 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3166.0173 | 165.04 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5497 | 478 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6380 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7789.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.6 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.65 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.88 | 60.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.7533 | 50.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 146 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.01 | 141.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.64 | 86.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.35 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 357 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 367.9999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 555.1 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 559 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 656.9999 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 691.5999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 917.9331 | 281 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 982 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1111.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1840.5333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12477.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37736.4 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63042.9666 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.6666 | 34 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 82.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.25 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.4 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 130.4999 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 239.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 336.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 485.1666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 872.6666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 886.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 910.4166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1442.7166 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1658.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1703.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1751.913 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3692.0191 | 172.39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.7666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 258.3333 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 487.404 | 90.26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57.9666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2465 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 18165 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5148.2771 | 284.96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.418 | 50.38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 350.14 | 8.54 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 592.1666 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1040 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 374.7833 | 199 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1289.1666 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.4 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 209.1 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 300 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231 | 20 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3394.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 99.9 | 99.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 75.25 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 100 | 12.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 82.4083 | 89.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 675.25 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 1323 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.9833 | 83 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 332.4999 | 210 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 468 | 117 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.5333 | 109 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6119.8639 | 158.82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 119.1666 | 110 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 349.9999 | 210 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3542 | 161 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 142.3613 | 152.53 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 781.3119 | 215.04 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 959.6345 | 285.04 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4144.4533 | 170.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.9999 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4399.5 | 210 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.35 | 83 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 288.9999 | 255 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 492.4289 | 82.53 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 604.2499 | 290.04 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 140 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 516.7499 | 117 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189.4665 | 232 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1714.4239 | 115.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1972.857 | 173.82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.4998 | 330 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1629.75 | 265 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2962.1166 | 107 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.5 | 30 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 88.1666 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 956.25 | 85 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 313.0479 | 172.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 619.9999 | 186 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3634.3309 | 158.82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3640 | 160 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3944.178 | 163.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5380 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.75 | 75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.3333 | 86 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.8 | 113 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.2693 | 88.82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325.04 | 325.04 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1166.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3599 | 122 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2082.4999 | 210 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10196.3332 | 260 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324 | 18 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410.7499 | 159 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1398.6 | 42 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6593.5426 | 291.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 448.5 | 115 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 766.6666 | 230 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.6 | 99 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2719.5 | 42 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450.5 | 106 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 455.4 | 69 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2593.9999 | 120 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1299 | 90 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 474.8666 | 68 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 524.1166 | 59 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.3332 | 140 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 35 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 569.3333 | 80 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.4167 | 5 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.8 | 106 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.75 | 15 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1110.2 | 61 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 25 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.5 | 10 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35 | 35 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.55 | 73 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.3332 | 140 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.6666 | 80 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.9666 | 61 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.8 | 117 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 208.8 | 29 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.25 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.75 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 656.8416 | 52.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.1667 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.8666 | 104 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.5333 | 86 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 235 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 20 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.7 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.1 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 481.4 | 116 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.5 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 270.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384.9999 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.25 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.75 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.7 | 138 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.5833 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.0166 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.2 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 847 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 349.86 | 7.14 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 265.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 619.18 | 7.46 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171.7333 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.5 | 75 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 267 | 534 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 579.3333 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1260.5999 | 198 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.25 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.3333 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.7667 | 47 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26079.75 | 335 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 197.0833 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 224.5 | 10 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375.9166 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 819.66 | 71.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 270.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.4 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1123.75 | 145 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.3833 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.5833 | 95 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.139 | 97.13 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1031.25 | 125 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 20 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.3333 | 56 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.3333 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.8666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.25 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.75 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.2 | 84 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.8333 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.9999 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1436.75 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.4 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.7666 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.8178 | 53.57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 396.6666 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6080.1 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.6 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 228 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243 | 405 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 401.5333 | 76 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.9 | 48.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 12 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56 | 56 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 220.2666 | 112 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 852.5 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5974 | 116 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.53333 | 8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.8333 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.9999 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.3333 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1640 | 328 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6667 | 22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.1666 | 127 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.2166 | 127 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.2 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.6 | 142 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.2333 | 82 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 583.3333 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 475.8 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 520 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 469.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 511.3333 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.8 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.0833 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395.01 | 59.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 609.3333 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.8333 | 113 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.85 | 319 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.8 | 254 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 440 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.2733 | 34.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.8333 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1797.9 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.75 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6324 | 136 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.4183 | 24.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.915 | 9.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.2715 | 24.13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616.1484 | 115.89 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 718.5597 | 255.11 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.7025 | 29.13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 660 | 90 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 783.75 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7547.7332 | 128 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.3999 | 78 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.739 | 29.13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140.97 | 114.3 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2211.9998 | 240 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.4563 | 24.13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 695.0133 | 107.2 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207.8999 | 81 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 543.8333 | 130 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.652 | 19.13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4864.1666 | 130 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2386.1 | 446 | 1 | 1 | 0325-Pulverizer skidding | U1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 638 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 768 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.5 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276.5 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 308.75 | 48.75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 513 | 114 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 686.3333 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1845.6666 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 697 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2056.6667 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.346 | 15.54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.9166 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 614.3332 | 194 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6409.3333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.5 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 390 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57.4166 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.0833 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 259 | 185 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1748 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 144 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 803.8333 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720.1666 | 290 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 365.5833 | 107 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 329.3333 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 862.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 270 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1722.7066 | 109.96 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3885 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5184.7333 | 166 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.75 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 561 | 340 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 135 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145.9999 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.8333 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 168.9333 | 28 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.4 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 252.0831 | 275 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 467.4999 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 406.3666 | 146 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 632.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1252.5 | 167 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4140.5 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85 | 340 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 428.2666 | 88 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.7 | 9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 301.7333 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1454.8333 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 718.58 | 23.18 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.4 | 18.68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 546 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.1167 | 13 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.6665 | 265 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.6333 | 41 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.25 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 222.3333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 436.5 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1495 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.2966 | 67.96 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.2 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1543.9999 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2213.1666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5713.4666 | 146 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.5 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.5 | 46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2048.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2159 | 68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.25 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 66.5 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 481.2499 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 488.75 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 294 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 301 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2200.9333 | 136 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 217.4666 | 56 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 585.0833 | 119 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 853 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 360 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 306.9166 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.25 | 125 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155.1666 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1182 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1426.1666 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.4998 | 330 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.5 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 379.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 522.6666 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 525 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1950 | 600 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.15 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132 | 22 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252 | 12.6 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 238.3333 | 220 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 463.75 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 152.1666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 184.8666 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.3333 | 88 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 218.05 | 89 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 395.68 | 49.46 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 435.0666 | 104 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 891.3332 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 922.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 900.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 272.1666 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.6666 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93.5 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115.5 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2817.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.8 | 72 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.25 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.25 | 103 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.9333 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 72.8 | 112 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.6667 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 237 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159 | 53 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 452.6666 | 97 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 960 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 203.9999 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 462 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.8 | 72 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1384.5 | 117 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1042.7666 | 218 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.96 | 10.12 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1711.4027 | 290.89 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 560 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.8 | 63 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 151.05 | 57 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 552.0832 | 265 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1082.0833 | 175 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1657.095 | 74.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 900 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.5 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 866.3333 | 92 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.4 | 51 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.9166 | 113 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 950 | 75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.2 | 36 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.65 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.5 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.6666 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1660 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3339.95 | 67 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.3 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 235.125 | 27.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3559.5 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 735.75 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.4799 | 114.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.8333 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.3333 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 140 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 459.3333 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 805.8333 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.6667 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2571.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 381.2428 | 74.51 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 249 | 83 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154 | 14 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 332 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 876 | 219 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118 | 59 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200.4166 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2101.9833 | 43 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 426.6667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.45 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.5833 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220.7666 | 74 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 410 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 474.9533 | 149.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51.5 | 103 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204.9666 | 43 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.5 | 135 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 278 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.5333 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.05 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 409.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 662.97 | 94.71 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 933.3999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1193.4 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.1 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.231 | 120.66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.0167 | 23 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 484.0166 | 113 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1020.8333 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.1666 | 103 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.3333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.7333 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78.4667 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 247 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 689 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1017.5 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1653.75 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2238.5 | 242 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3354.07 | 176.53 | 2 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4039.1664 | 370 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.35 | 11.85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 518.01 | 16.71 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 906.12 | 16.78 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.5833 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.5332 | 158 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 514 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 893.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1274.3999 | 162 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1710 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.6667 | 23 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8333 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.8166 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 322 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 532.5 | 142 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 213.4 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 491.3333 | 67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2957.4999 | 390 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 186.15 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 343 | 12.25 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 390.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.8 | 18 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.4332 | 218 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.265 | 27.1 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170.3 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 441.4498 | 243 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1223.1996 | 528 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2790.6666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5491.6665 | 500 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.8833 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.0999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.3999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 796.9166 | 131 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.54 | 20.6 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.4999 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 206.7 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 572 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 606 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 725.4 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 799.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1239.5 | 67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11630.3332 | 230 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 282 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 24 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 484.9 | 18.65 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165 | 165 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 440.8333 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.8333 | 118 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.1333 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.5333 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.9331 | 401 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2626.2399 | 139.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.85 | 63 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.3333 | 118 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.2 | 198 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.3333 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 193.7 | 149 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 393.6833 | 79 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1102.5 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1345.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.386 | 63.72 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1892.9 | 41.15 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 302.88 | 37.86 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.1667 | 17 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 521.5101 | 99.97 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.3 | 201 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119.6 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.7 | 163 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 370 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 476.2666 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 920.4 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1027.3333 | 92 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.8 | 24 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.3333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.65 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 289.7333 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370.6 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.8665 | 208 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51.9999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 461.8333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 596.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 723 | 241 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7700 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 426 | 6 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 899.4166 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.5 | 138 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.7 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.9999 | 300 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.7997 | 378 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1470 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.9999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.0833 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306.8 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 389.7 | 18 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1157.3333 | 112 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.9999 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1138.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2977.61 | 17.83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 581.0833 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1637.9499 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.6 | 6.32 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 809.16 | 12.26 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133.25 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 546.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.6 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312.5 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 406.7 | 42 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 422.2641 | 146.45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 493.0666 | 86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 686.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 845 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 927.85 | 77 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1330.56 | 110.88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.4 | 294 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 199.4666 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 207.4166 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 348.0666 | 227 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 402.4 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 556.15 | 227 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.7686 | 71.98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1038.3332 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1695 | 226 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2061.8 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.0664 | 328 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.4166 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.75 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 249.0832 | 245 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 598.5 | 126 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.5333 | 23 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.75 | 23 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.6 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.9 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.5 | 178 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 521.5 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 894.6666 | 122 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76.5 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 50 | 2 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 351 | 70.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 823.5 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1531.4999 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1560.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2750.4165 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 191.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3157.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 68 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.02 | 18.67 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.5 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.75 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 18 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 375.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.1667 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.1666 | 170 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 592 | 64 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.9166 | 31 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 288 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 181.7666 | 82 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2932.5 | 69 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.1833 | 67 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278.25 | 105 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 655 | 60 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.5999 | 114 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236.8666 | 323 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 213.2161 | 216.83 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 217.458 | 161.08 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4079.01 | 209.18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.1666 | 62 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1689.7 | 122 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1042.1666 | 130 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 396.2 | 56.6 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.0617 | 7.3 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.8333 | 55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 465.3999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 67.6666 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.9999 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.1666 | 95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.2 | 63 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.01 | 57.48 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.5 | 69 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1137.7 | 62 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 745.6165 | 539 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35946.1664 | 770 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.0666 | 148 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 462.9103 | 106.01 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1974.1666 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.5 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 251.0833 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2026.35 | 106.65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.9999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221.25 | 59 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176.4166 | 145 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 657.8 | 69 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D3-Forced - Postponed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.3333 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230 | 150 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153 | 51 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1236.75 | 291 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27790.8473 | 112.09 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.8 | 9.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 102.9166 | 95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 256.2 | 84 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293.5333 | 37 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 508.7833 | 49 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1709.8666 | 64 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1094.5833 | 71 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1710 | 900 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.6 | 24 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 352 | 88 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 547.2 | 38 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 594.9166 | 59 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6130 | 40 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.2667 | 44 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1319.885 | 26.31 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 814.9166 | 77 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23039.25 | 51 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259 | 37 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 382.7999 | 99 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81 | 54 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240 | 30 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2860.25 | 51 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4534.3333 | 61 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163.8 | 84 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 552.5333 | 74 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1917.63 | 40.23 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 1 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2203.1166 | 61 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4311.9999 | 96 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 10 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 256.5333 | 74 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 226.6 | 113.3 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 972.1286 | 69.77 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.1666 | 59 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3336 | 72 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4833.3713 | 117.22 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.8 | 28.2 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4192 | 32 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4316 | 40 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45238.5091 | 149.59 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76.7 | 39 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.3166 | 79 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153 | 34 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240.5333 | 44 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8186.88 | 33.28 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 735.08 | 31.96 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3307.4166 | 43 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.7333 | 44 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154 | 84 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238 | 56 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23583.777 | 36.89 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126730.2663 | 568 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.7997 | 408 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 230 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 258.1 | 178 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 329.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 528 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 581.3333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 702 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1715.5 | 365 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1915.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2077.3333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6765 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7841.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17808 | 126 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.4 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.3333 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.5 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 236.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 488.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 555 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 604.1665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 882 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 891.8166 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1070.55 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1280.202 | 58.68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1845.486 | 58.68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5550 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5725 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.7333 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.4333 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209.55 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1190 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Winter | 213.3949 | 140.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1168.5 | 155.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 345.1666 | 95 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.6665 | 265 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 945.1665 | 265 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1133.8433 | 21.4 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1316.1665 | 265 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1785.7332 | 236 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133846.05 | 117 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13147.3331 | 410 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.5 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.4 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.3333 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 287.8666 | 254 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 291.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312.6499 | 111 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 374.8872 | 146.06 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 564 | 282 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1350 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4590 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10065 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.75 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 317.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 383.9166 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.6666 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450.5 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 577.5 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 674.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 791 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1691.6665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2557.0266 | 155.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.3333 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 594 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 612.5667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 837 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3326.3332 | 340 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6914.4 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184.8 | 23.1 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 776.7833 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.4999 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.1667 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.8332 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 214 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 239.9833 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325.2666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 403.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 560 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 897 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1164.8331 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1544.25 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1728.1983 | 107.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3318.8999 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4895 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8617.8331 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50007.7499 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.2499 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 650 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1657.6833 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1694 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6066.25 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.3666 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.7333 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.5 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 346 | 173 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 618.5666 | 154 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 751.3333 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 939.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 954.1665 | 229 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3040 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3072 | 320 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4060 | 112 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15842.6666 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 997 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1906.275 | 254.17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7816.4333 | 241 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8538.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1954.9665 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.304 | 34.13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.5 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.1 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 138.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.5 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 390 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 433.3332 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 880.8665 | 292 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 956.75 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1136.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1266.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2103.9666 | 127 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4052.0833 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6637.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.8333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.3333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.7667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.5 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 274.6333 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 329.1665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 409.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.5 | 315 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 667.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 726.75 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 869.4 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1017.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1386.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1808.3332 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3787.5832 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4095 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.5 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6667 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.25 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 270.1733 | 88.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 935.1333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1143.4665 | 268 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1381.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1662 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2635 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4550 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7141.4666 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10922.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11010 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 325.3799 | 287.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 738.815 | 268.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 22 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2338.05 | 117 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.9 | 17.9 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4210 | 120 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1351.25 | 575 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11469.9996 | 600 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4747.5997 | 858 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.2499 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.9499 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 144.0833 | 247 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.9166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 462.6833 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 964 | 241 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1215.45 | 111 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1500 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1711.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1834.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1895.8332 | 325 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 230.4041 | 50.27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.9166 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375.6 | 93.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 399.6666 | 218 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 563.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 695 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 895.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1371.4258 | 85.27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1770.1666 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2190 | 365 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2301.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2437.9666 | 122 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.2 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.8333 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 318 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 403.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1140 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1779.3332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2226.6666 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2799.3333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6900 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1454.1 | 484.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.014 | 58.26 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.0667 | 21.4 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.405 | 33.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.2833 | 91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.3833 | 101 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 159.8 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.3333 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 459.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 661.5 | 294 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 949.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1836 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1940 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2506 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2623 | 244 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.45 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.3167 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53.3332 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.4999 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.9333 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.25 | 80.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 316.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345.5833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 515.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 745.1966 | 152.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1041.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1175.9998 | 360 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2014 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2310 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 147.6 | 123 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 172.5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 338 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 635 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 953.25 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3375 | 450 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 360.465 | 205.98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 697.565 | 253.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 785.4 | 36 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1488.37 | 21.4 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 820 | 100 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6454.3332 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 400.4333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 591.4999 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 639.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 936.7165 | 217 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2780 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2828.2499 | 405 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5879.9 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6490 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.048 | 60.48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.6666 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 171.7333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 294.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 442 | 88.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 451.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 511 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 588.8 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 658.3333 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 750 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 785.6332 | 182 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 859.75 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1137.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1250.3333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1281.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3080 | 112 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6374.75 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10415.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10859.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.4667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180.55 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 204.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 280 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 536.55 | 219 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 538.45 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1712.1166 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.4257 | 22.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 117.5333 | 86 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 45 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4719 | 117 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 354.9333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 269.9911 | 136.13 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1198.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 98.3329 | 590 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9100.845 | 549.9 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.4166 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.9 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 365.0666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1010.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1013.3333 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2231.6665 | 325 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10240 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.8333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.9 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.5 | 230 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 694.33 | 152.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2496.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.9516 | 56.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.4906 | 60.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92.7 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 139.3333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 260 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 703.1734 | 80.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 987.6 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1207.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1629.6 | 112 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2000 | 500 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11712 | 122 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.8477 | 257.11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6212.5 | 710 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2299.7332 | 448 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1147 | 31 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 629.3666 | 79 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487.6667 | 35 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2211.0828 | 785 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.75 | 45 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 889 | 127 | 1 | 1 | 0342-Pulverizer inert system | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 745.3333 | 172 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 402 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 470.0498 | 564.06 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 835.532 | 187.76 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 544.6666 | 76 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 516.8 | 51 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.9999 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5993.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.1666 | 118 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1657.5 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19857.1333 | 68 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2089.5833 | 125 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.74 | 44.4 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.8 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.06 | 3.63 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123 | 123 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.8 | 108 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 659.75 | 87 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1265.3333 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2936.7 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 395.8999 | 222 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3152.5 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 313.2 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 383.5 | 118 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.5 | 135 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6209.9166 | 215 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1131 | 60 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 247.8667 | 11 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1729.3333 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.5333 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 241.9 | 118 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3160.3333 | 190 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.8333 | 110 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 239.5832 | 125 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46 | 120 | 1 | 2 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3009 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 10 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 166.2666 | 344 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 493 | 29 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.1666 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1017.76 | 127.22 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1376.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.3333 | 43 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72 | 90 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.9999 | 150 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 450.0333 | 46 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2623.5 | 110 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3523.5 | 145 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 731 | 85 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.25 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 711.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155.35 | 71.7 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1733.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35 | 35 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.8 | 31.2 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 103.5 | 115 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 693 | 45 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 353.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 736.45 | 33 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.8333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1160 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4414.8 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24480 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.3333 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211.8666 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 450 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 585 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 336.3 | 59 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 973.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 739.0666 | 46 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1903.7332 | 472 | 1 | 1 | 0344-Pulverizer inspection | U1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.2 | 36 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.7999 | 96 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 662.6666 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 831 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.3332 | 200 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 339.57 | 59.4 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 468 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 847.1666 | 85 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 684.0666 | 62 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 780.75 | 45 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 136.85 | 21 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 348.5833 | 47 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 368.7667 | 26 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1120 | 70 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6880.9666 | 62 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 539.9666 | 97 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1600 | 320 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2534.1667 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9945.47 | 30.3 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 702 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27895.1667 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1139 | 8.5 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2992 | 34 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.4167 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2492.9333 | 56 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16037.3331 | 320 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1616.1633 | 31.1 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5985.95 | 57 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 959.76 | 34.4 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2928.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2878.8 | 72 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2035 | 370 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4880 | 64 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6744.5 | 82 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1231.25 | 25 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.7667 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.5333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 406.3 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 692.1166 | 131 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199.5655 | 323.62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 288.0666 | 149 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 825 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1566 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.2253 | 31.64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 152.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.4 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.5333 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51 | 5.1 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 593.9505 | 101.53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.6666 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.5333 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.7999 | 132 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.6667 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.1333 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.85 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85.5 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 147 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.1 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 633.6257 | 242.15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 886 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99.6666 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.61 | 74.04 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.3833 | 11 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.4166 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.95 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.4 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 895.2332 | 502 | 1 | 1 | 0346-Pulverizer pyrite removal system | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.75 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.7 | 9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1387 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2555 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3420 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305.28 | 33.92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.3 | 26.65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 375.7 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.5 | 50 | 1 | 2 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.4666 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62.8333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.1667 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.1333 | 76 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104.8666 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.8666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.3333 | 10 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.5 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.8333 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.1 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.3333 | 10 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.87 | 23.1 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 271.4 | 118 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 408.3333 | 250 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 149.01 | 49.67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 579.9998 | 240 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.5333 | 82 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10295.4999 | 177 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 891.25 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 675 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.9667 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.9833 | 83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.9666 | 103 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.5 | 10 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.1667 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 149.1 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80.2333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 142.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.1 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1941.9666 | 149 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.25 | 165 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.0833 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.7 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.3333 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.7333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.25 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.25 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.0667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.5 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.1 | 87 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.3374 | 122.55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 484.5 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4887.6665 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 202.9999 | 210 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 298.095 | 198.73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 825 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.9999 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.6333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.2667 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.15 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.9166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1050 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4536 | 168 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.3333 | 32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 504.1666 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2112 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.8332 | 155 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1767.8999 | 159.75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70.2333 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.15 | 9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.2 | 16 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.3 | 18 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.75 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1411.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4266.9999 | 255 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4478.8856 | 333.83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 287.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3361.6 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.7 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.7 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.6 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.1667 | 13 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 136.6833 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 896.1666 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.3666 | 105.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.2166 | 89 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33046.4876 | 333.41 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 84 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 724.5332 | 152 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1875 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.5 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.75 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 394.3333 | 13 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 411.3999 | 132 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1817.1333 | 97 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.9767 | 14.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1093.644 | 107.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.1666 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3218.9999 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 249.1666 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.65 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2077.3332 | 328 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.7 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 418.8999 | 177 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 600 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 648 | 162 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1852.8167 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.6666 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209.55 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 354.1665 | 250 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 533.3405 | 138.53 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4034.825 | 62.75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.0833 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2141.3332 | 352 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.7166 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 223.2 | 248 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2809.7666 | 97 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6645 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 287.6041 | 62.75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.4 | 48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 807.8498 | 321 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1688.48 | 276.8 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2014 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7364.4998 | 330 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.5 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 139.1999 | 288 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 484.2208 | 62.75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1657.9166 | 115 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1026.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 425.75 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250.6666 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 366.3332 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475.193 | 221.02 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 999.9166 | 169 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1075.7666 | 118 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1375 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1062 | 177 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72 | 54 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87 | 87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 386.1666 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2329.25 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4403.1666 | 290 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 17 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.8667 | 4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.3567 | 40.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480.25 | 113 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.2999 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499 | 499 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 343.2 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.2667 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.8499 | 147 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 36 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.4 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 289.5 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.6666 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.15 | 87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1184.4166 | 233 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1385.4166 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3815 | 109 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1785 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.1333 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.75 | 99 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 427.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 616.5666 | 106 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7237.5166 | 227 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7478.75 | 193 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 761.04 | 27.18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1458.7664 | 818 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 104.9666 | 67 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2977.8482 | 301.3 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1192.5 | 530 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 703.5 | 33.5 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4971.6666 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 284.25 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 87.4999 | 375 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 144.1664 | 346 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 200.6665 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 344.3533 | 62.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5870.3164 | 469 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 553 | 395 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 100.5333 | 104 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1414.5 | 410 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5420.7996 | 528 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3788.0864 | 376.3 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.15 | 69 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 473.6 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.4166 | 65 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 12 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 114.3999 | 132 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 336.5333 | 32 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 449.5 | 310 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 513.5 | 395 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6743.1 | 546 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 13.6665 | 410 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1399.6665 | 380 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 282.5 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1190 | 119 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 107.3332 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 242.6665 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 5.2498 | 315 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 388.4999 | 315 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 34338.3333 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2521.3332 | 310 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14599.3331 | 305 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1260 | 42 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7222.1331 | 742 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 725.3332 | 340 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 854.5332 | 442 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 784.75 | 73 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7865.0998 | 243 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15130 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 25.2664 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 205.2 | 342 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 31.4166 | 65 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 131855.5499 | 207 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 24.2666 | 52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 369.87 | 369.87 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 216.9867 | 16.48 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270.2499 | 345 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 512 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 512.5 | 125 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5834.4 | 528 | 1 | 2 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 262.4167 | 47 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 138.1053 | 147.97 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1324.2664 | 382 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 0 | 0 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 13.2 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 379.8499 | 321 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1181.4999 | 417 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4194.7498 | 315 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1006.2498 | 345 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.5 | 394 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38800 | 400 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 18.25 | 73 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 168.6666 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1450.6665 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 5603.0833 | 71 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 48728.5832 | 547 | 1 | 1 | 0359-Gas burner piping and valves | U3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 146 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 63.75 | 255 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 83.25 | 333 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 319.7998 | 369 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2074.4999 | 270 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 49.1666 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1597.6832 | 373 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15697.3331 | 610 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 940.6664 | 340 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2217.7999 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 752.4998 | 258 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 61.6 | 56 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1916.6 | 518 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 19.6 | 33.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 95 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 25 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 882 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 32.5 | 39 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 81 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 177.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 258.3333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2513.532 | 91.07 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 43.2 | 16 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 54.0833 | 59 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 70 | 21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 433.3333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 159.8566 | 44.2 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3272.4 | 303 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 2050 | 82 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 262.5 | 12.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 906.1 | 82 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 50.7 | 78 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 643.75 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1551.6667 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 21.15 | 14.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 26.814 | 44.69 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 68.445 | 16.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 60.9166 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 48 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 381.5333 | 97 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 266.9333 | 88 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1757.7083 | 76.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3241.6666 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 113.9999 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 61.8333 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 625 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 654 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 27.3933 | 5.87 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1513.3066 | 73.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 177.6333 | 73 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 16.5917 | 18.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 315.4 | 57 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 57.3167 | 19 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 35.65 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 201.175 | 19.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 27.569 | 43.53 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 59.1666 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 69.5933 | 14.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 237.51 | 4.06 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 625.9167 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 168.63 | 102.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 165 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 345.7667 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 12.19 | 13.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 30.9833 | 13 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 6558.98 | 85.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 10.3333 | 31 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 1601.75 | 74.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 860-Co-generator Block
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 860 | Co-generator Block | WECC | Summer | 1023.1333 | 74.5 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 860-Co-generator Block
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 286.3666 | 78.1 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 861-CoG GT units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 218.68 | 78.1 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 861-CoG GT units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 232.9983 | 78.1 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 861-CoG GT units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3384.7 | 34 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3196.4999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 305.0666 | 143 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 14.4999 | 174 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 548.5333 | 121 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2126.575 | 40.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2685.4216 | 70.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 394.3333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.88 | 2.24 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.08 | 3.46 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 907.2 | 6.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1499.9998 | 450 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21202.4997 | 450 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.6 | 156 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 358.8 | 552 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348.3333 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14631.4666 | 64 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.25 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.6667 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 101.2 | 69 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 48 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11383.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 378.7166 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.99 | 6.11 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.21 | 6.47 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.46 | 5.02 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9492.1166 | 197 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 309.6 | 7.74 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134152.8332 | 430 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1329.4166 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 195.6166 | 121 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 483.7999 | 177 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2490.8999 | 342 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 54.8667 | 4 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.44 | 38.62 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 390.5 | 110 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.6666 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 302 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 746 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 198.1666 | 290 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2819.05 | 39 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 206.6666 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.05 | 3.87 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 732.9 | 6.98 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.0665 | 277 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 668.3 | 163 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 94.5166 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 172.9833 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 5408.9634 | 406.18 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 377.0833 | 125 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5167.2 | 144 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29410 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.665 | 9.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14498.6833 | 61 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.7333 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56 | 42 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.3332 | 125 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 574.5 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 55.0333 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.02 | 2.91 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 246.4 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 324.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 3.2 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 9.775 | 3.45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.94 | 5.38 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 150 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.28 | 17.83 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9512 | 164 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.96 | 3.08 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3380 | 650 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 781.9996 | 552 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4364.4998 | 258 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.2333 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1650 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 39 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 773.7666 | 139 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.8333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 342 | 114 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 850.6666 | 145 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3517.1665 | 449 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6367.5333 | 44 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 180.6667 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 7.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 827.52 | 25.86 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 654.4999 | 330 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.4833 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.0333 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.9 | 123 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30458 | 194 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 689.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 996.8667 | 19 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.85 | 5.05 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.66 | 2.94 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32400 | 450 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 561.6 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 252.3 | 58 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 392 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 13025.6333 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 400.1667 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 377.7667 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 252.0833 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 927.0567 | 41.51 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 195.8833 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1604.1596 | 76.51 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 35.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1622.1267 | 14.57 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 14.3272 | 14.57 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1549.7623 | 14.57 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 712.3478 | 321.36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2330.5333 | 22 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 8264.3468 | 14.57 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1620 | 324 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 187.7233 | 56.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 191.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 19.25 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 330.1 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 464.05 | 3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 909.7 | 22 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4604.2333 | 58 | 1 | 1 | 0360-Burners | U3-Forced - Postponed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 1221.8666 | 58 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1527.8363 | 19.09 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 10824 | 22 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.212 | 18.96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 234.0499 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 11.9233 | 35.77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 166.2 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 203.5833 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 182.4165 | 199 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 67.2 | 72 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2525.1293 | 15.31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 395 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 170.5 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 106.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 27.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 66.2358 | 13.03 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3160 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4.25 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 176.4 | 168 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 321.305 | 17.9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 408.2599 | 164.4 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 67.6833 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 9011.982 | 17.64 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 7.5167 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 14.9999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 41 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 558.3333 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3349.7333 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2018 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 32 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 564.6667 | 30.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5.9999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 398.3333 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 10.8499 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 14654.6208 | 9.25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 159.8666 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 23.2333 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3560 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 367.5 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1554.5833 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 860 | Co-generator Block | RFC | Summer | 1582.7 | 119 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 19.55 | 51 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 860-Co-generator Block
0361 | Burner orfices | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2018 | Gas | OG | 850 | Combined Cycle Block | WECC | Summer | 9492 | 240 | 1 | 1 | 0361-Burner orfices | SF-Startup Failure | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16119.8333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 497.0666 | 128 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3605.65 | 111 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 749 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 58.9333 | 104 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94.0333 | 91 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 114 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5588.9166 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 196.1663 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.1999 | 228 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92.0766 | 120.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2117.5 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 29.3766 | 125.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 64.6 | 51 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 580 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111.6662 | 670 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8097.6 | 723 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 413.4 | 156 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2768.4998 | 339 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 434 | 434 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.9999 | 120 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3480.5331 | 832 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 717.25 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2389.815 | 20.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 503.25 | 183 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.6 | 88 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 320 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 366.1664 | 845 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 864.5 | 130 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14763 | 228 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 459.1665 | 190 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1160.2582 | 376.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.3666 | 146 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1496.3331 | 670 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 781.3832 | 271 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.0666 | 116 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 123.5 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.25 | 135 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 94.6033 | 20.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 525 | 500 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 613.35 | 423 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 143.5 | 205 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.9666 | 83 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 409.3332 | 307 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 145 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 50.6 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 102.955 | 34.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 43.9166 | 31 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1615.3667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 223.3 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1140 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 434 | 155 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 257.25 | 63 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 572 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 41.25 | 11 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 169.1333 | 47.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 106.4 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 240 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 20.5633 | 39.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 822.2667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2014.9999 | 150 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 3.2667 | 9.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 66.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1.8667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 165.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 602.6666 | 160 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1117.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 22.5533 | 39.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 524 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 10.7333 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 141.6333 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 60 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 21.15 | 9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 6.0667 | 2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 65.6633 | 196.99 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 211.6667 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Winter | 109.4999 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Winter | 18766.9166 | 347 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 5486.6667 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.212 | 18.96 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.775 | 27.75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.8467 | 28.85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 12.954 | 43.18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 45.12 | 37.6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 245 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.246 | 32.46 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 58.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 788.9 | 42 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Summer | 106.995 | 61.14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 27.3381 | 26.89 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3981.2333 | 41.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.6227 | 22.48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.1745 | 27.21 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.1768 | 27.23 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.2585 | 27.93 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.6893 | 20.08 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 73.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 606 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 832 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 95.3167 | 19 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 8.4 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 14.44 | 10.83 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Summer | 132.92 | 66.46 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Winter | 311.4999 | 105 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 36.4 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.528 | 18.96 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.9155 | 24.99 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.552 | 26.64 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.8021 | 32.59 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.8053 | 28.54 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.7383 | 28.43 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.1213 | 38.41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.31 | 35.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 8.8666 | 76 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 199.6633 | 39.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 740.6166 | 37 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Summer | 280.5 | 110 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.8082 | 24.07 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.0915 | 35.07 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.235 | 18.15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5.0666 | 76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 10 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 24.0666 | 76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 114 | 76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 205.8333 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 329 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 6.3333 | 76 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7.5146 | 28.18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 24.5 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 31.35 | 19.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 76.89 | 19.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 43.3333 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 89.1 | 81 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 708.5 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.16 | 18.96 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3.8 | 76 | 1 | 3 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.8105 | 32.07 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 9.1 | 42 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 54.1333 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 138.39 | 131.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 203.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.905 | 29.05 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 38.5417 | 46.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 339 | 33.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.8983 | 35.39 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | NPCC | Summer | 24.45 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 862-CoG steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 981.3333 | 160 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6638.8331 | 610 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1535.6 | 139.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70093.5 | 415 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 141.8664 | 448 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1416.6665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1495.8332 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 104.5 | 190 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.075 | 120.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 49.8667 | 44 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2667 | 8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77 | 77 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 41.6665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 470.8333 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 637.5 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19380.6999 | 174 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2957.5 | 455 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60.8 | 38 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 278.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.9998 | 300 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 121.333 | 455 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 674.9165 | 455 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3404.9165 | 455 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8043.75 | 825 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 194.4333 | 38 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 328.57 | 113.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5442.75 | 615 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 250.1667 | 38 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55 | 220 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.9166 | 85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.3333 | 56 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 25 | 60 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 60 | 60 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 166.833 | 455 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 521.1665 | 295 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 82.7 | 82.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 33.3332 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 21485.2498 | 243 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 905.1 | 431 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 19.8 | 44 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.3333 | 34 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 40 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 371.85 | 37 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 335.2666 | 188 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 600.3832 | 221 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2904.5332 | 448 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1496.0962 | 406.18 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7955 | 860 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5849.2497 | 495 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5090.1332 | 256 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 9722.2663 | 568 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 218.9499 | 87 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 1511.5833 | 85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 108.5 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 37.5 | 75 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13.5 | 54 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 32.0833 | 35 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 197.8 | 86 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 97.6 | 24 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 36.8333 | 85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 61.8333 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 108 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 297 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 74.385 | 17.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 43.6667 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3.1358 | 37.63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 30.38 | 45.57 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 32.14 | 48.21 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3.3525 | 40.23 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 91.1667 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 450 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 7.5 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2.3167 | 13.9 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 47 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 11.1767 | 33.53 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 495 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 438 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 770.4 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.4666 | 52 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.0666 | 154 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.9635 | 136.49 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 201.9332 | 233 | 1 | 2 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 211.25 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.1666 | 130 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36 | 120 | 1 | 2 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.9999 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.9999 | 90 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.5 | 170 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 285 | 190 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 461.5499 | 153 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8342.3331 | 580 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2200.5 | 815 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.4166 | 131 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 285.5619 | 120.66 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.5 | 150 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.5 | 110 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 408.3333 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13 | 65 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72 | 240 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25 | 75 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18980 | 650 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8432.5163 | 589 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3630 | 363 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 283.8 | 258 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186 | 93 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424.2349 | 106.95 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.1333 | 163 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 311.6 | 152 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1529.3667 | 11 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 524.6907 | 168.35 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.4999 | 150 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.7499 | 105 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.9999 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2351.25 | 475 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1845 | 820 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 460.0999 | 258 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22405 | 60 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1009.1667 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 15.3333 | 23 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 302.4999 | 165 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.5833 | 85 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35 | 105 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3534.9998 | 606 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 253.9831 | 311 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 389.424 | 243.39 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1127.3333 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.1666 | 110 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.6666 | 115 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 285.8332 | 245 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.5 | 70 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23793.3328 | 830 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 931.6998 | 363 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.5 | 65 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 125 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.4 | 72 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 208.4166 | 61 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66 | 110 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23 | 115 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28 | 70 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.3333 | 115 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15.1666 | 70 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.6666 | 170 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 106.5333 | 47 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4891.3329 | 638 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.4166 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.6666 | 50 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.0833 | 5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.3333 | 250 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339 | 113 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 520 | 130 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.5 | 110 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21 | 70 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.75 | 85 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.8333 | 95 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1229.833 | 470 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.75 | 45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.3332 | 140 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.8 | 11 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 369.6 | 168 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.75 | 85 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.3333 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.3333 | 50 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.6666 | 110 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.9999 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 237.5 | 95 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28415.8329 | 650 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.6 | 306 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 150.1666 | 170 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 6 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 84.15 | 27 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165 | 220 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1069.9999 | 75 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 555 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 426 | 72 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2352 | 14 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97 | 194 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 412.5 | 150 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.6 | 169 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9256.0999 | 294 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 447.5 | 25 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 144 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.8665 | 244 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 826.5833 | 65 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 886.8831 | 419 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 215.6667 | 20 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.48 | 186.37 | 2 | 2 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1613.3332 | 200 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1210 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74880 | 520 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 575 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36845.0832 | 415 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5513.9623 | 56.66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.25 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 16.5 | 16.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 22.8 | 8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 33.825 | 16.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 51 | 25.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 6.75 | 9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 9.2733 | 10.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 67.6 | 19.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 37.8933 | 23.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 22.8 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 178.6917 | 20.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.71 | 10.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 12.9333 | 9.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 61.875 | 16.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 11.5033 | 20.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 35.1 | 81 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 107.25 | 15 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137.8666 | 94 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 60 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.75 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.25 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 624.5166 | 101 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1504.9999 | 258 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 13.44 | 12.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 99 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 6.24 | 11.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 15.4 | 21 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 64.75 | 11.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 199.08 | 42.66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 9.5 | 9.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 15.3333 | 9.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 24.82 | 10.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 12.35 | 9.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 15.04 | 9.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 19.84 | 19.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 46.4 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 17.7833 | 11 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 31.25 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 343.4 | 51 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32 | 30 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215.94 | 106.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 46.55 | 10.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 179.4 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 67.6667 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 284.75 | 51 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.1666 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 877.387 | 30.66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1263.703 | 30.66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 85.5 | 57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.2 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 13.9167 | 16.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 42.025 | 20.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 7.6 | 8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 17.6 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 42.5333 | 22 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 43.3333 | 12.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 29.785 | 25.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 260 | 75 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.8786 | 40.66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 336.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 651 | 93 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 19.7867 | 22.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 190.85 | 33 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 349.9167 | 13 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 15.3367 | 10.7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 23.8 | 25.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 51.2333 | 26.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 4.95 | 9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 86 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 101.85 | 10.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 328.4667 | 26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 9.975 | 10.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.9083 | 8.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 63.2 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 98.8166 | 121 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 39.0833 | 67 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 961.3772 | 14.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5517 | 180 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 2329.4 | 76 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2510.4499 | 111 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Summer | 25.5 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1.327 | 26.54 | 1 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 14100 | 150 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1.307 | 26.14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 2998.2 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.1883 | 26.26 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2446.184 | 134.16 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 120 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 103814.1 | 342 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7.6285 | 8.03 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 387.3333 | 83 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 440.3 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2331.9333 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 7337.75 | 49 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 701.3802 | 33.11 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 4683.5773 | 247.59 | 1 | 1 | 0410-Other burner problems | U2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1.7526 | 26.29 | 1 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.1983 | 26.38 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7681.3333 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 935.4505 | 28.39 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 29.4667 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 0 | 0 | 1 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 13.6348 | 26.39 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 60.0288 | 26.29 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 62256.4 | 404 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 0.88133 | 26.44 | 1 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.674 | 26.74 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 35.4 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3333 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.3333 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.8 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.6667 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 131.6666 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.1666 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 434.5833 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1830.9666 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.4833 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 478.3333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 705 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2356.2 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8284.5 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 15.1667 | 35 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 126.85 | 43 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 141.1833 | 43 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.848 | 49.68 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 849.0166 | 121 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 944.6666 | 109 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1179.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4156.5 | 102 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.5 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 470.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.5233 | 55.51 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8.7 | 58 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 26 | 60 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3693.426 | 141.24 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 24 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.4 | 61 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156.7999 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.2166 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.99 | 25.33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 96.4166 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 968 | 121 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1365 | 130 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48667.7786 | 46.96 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 951 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1171.3878 | 68.17 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3638.3333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 266.98 | 38.14 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7.15 | 33 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 21.45 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1448.85 | 39 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 191.215 | 25.05 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 682.195 | 25.05 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.8 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.1 | 98 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195 | 195 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 292.25 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 560.7648 | 42.11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1764.1 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.0073 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.75 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222.25 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1080.9166 | 109 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2338.9333 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1811.3333 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6.9 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.75 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204.1667 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 496 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2451 | 45.6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.5 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47 | 11.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.5 | 109 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 223.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 978.0833 | 121 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 792.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3432.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2.8333 | 34 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3.4667 | 26 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4167 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.6666 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6666 | 58 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 992.8333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1944.5832 | 325 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19 | 4.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.6666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.01 | 17.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 416.5 | 119 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 455.895 | 30.7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 512.3333 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.1666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.0833 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.8 | 57 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155 | 38.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 433.1 | 142 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 442.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3.85 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30 | 72 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5593.14 | 135.1 | 1 | 1 | 0415-Cyclone feeders | U2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.4 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107.6666 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 198.6333 | 59 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1408.9166 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.5 | 114 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3791.0833 | 97 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4683.91 | 101.64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.9666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.854 | 85.96 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114.1167 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 635.25 | 77 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 77.0833 | 37 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3.3333 | 25 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7.15 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.25 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.9666 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.25 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200.6 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3395.4666 | 68 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.5 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.297 | 50.09 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 268 | 53.6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139 | 27.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245.5833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1664.5833 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 30.0333 | 34 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7.5 | 25 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23.4667 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 59.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 38.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 101.9667 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 33.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 14.7 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 36.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 10411.6164 | 439 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 961.45 | 469 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 745.3 | 514 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 785.75 | 449 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 960 | 200 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 706.9163 | 499 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60.4166 | 125 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 60 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1440 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1922 | 31 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2149.5833 | 25 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4655.4665 | 301 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1500 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2040 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 16.5333 | 32 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2774.3833 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1006.4666 | 62 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1050 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5285.15 | 39 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 249 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1650 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 699.1833 | 91 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 15.8666 | 34 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3853.55 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1723 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.0333 | 46 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123 | 60 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.3333 | 20 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3392.4333 | 49 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6625.17 | 736.13 | 1 | 1 | 0425-Cyclone dampers | U1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 39.75 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.5857 | 5.18 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 285.8333 | 35 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10240.5332 | 364 | 1 | 1 | 0425-Cyclone dampers | SF-Startup Failure | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 540 | 54 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14 | 60 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.6666 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 14 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 253.75 | 35 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.7666 | 86 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 25 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1549.05 | 449 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2892.1664 | 469 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 219.6 | 27 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9633.75 | 105 | 1 | 1 | 0426-Cyclone air ducts | U1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.3333 | 40 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6.0666 | 28 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 146.1833 | 49 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.8333 | 50 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6.45 | 43 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2678.3333 | 100 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 21.5333 | 68 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 48.75 | 75 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1.5 | 30 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3.6333 | 2 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 4 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130 | 13 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.2 | 39 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7533.9 | 54 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.9333 | 44 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.25 | 75 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.4 | 41 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80 | 40 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21798.3333 | 50 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 208.7458 | 71.57 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 20 | 40 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.4 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.0833 | 25 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.8333 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.1666 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3333 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6667 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.9 | 53 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.66666 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.0667 | 16 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.7333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.25 | 39 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.8 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.25 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.2 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.7833 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.8333 | 70 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.3499 | 147 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.15 | 23 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.3333 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.9167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6667 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.5833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6667 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 197 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.75 | 15 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8 | 24 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.2667 | 19 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.4 | 21 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.7 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.8 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.1 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.9999 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63 | 31.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.55 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181 | 45.25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.1333 | 17 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.6667 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 12.3666 | 53 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17559.7998 | 228 | 1 | 1 | 0435-Other cyclone problems | U2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.59999 | 18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.05 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3333 | 20 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.35 | 27 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3333 | 14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.8 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.35 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43 | 86 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.75 | 15 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.86666 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8333 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.3333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.75 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.4333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.9833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.3 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2010.9166 | 59 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.0833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.4 | 22 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.1666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.5 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.7833 | 53 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.5 | 15 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.75 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19 | 9.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.8333 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 578.0667 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.65 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.9 | 18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.4167 | 29 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4166 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.0667 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.4666 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.65 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.35 | 29 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.5 | 141 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 324 | 40.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14364.7666 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 20 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.3333 | 35 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.55 | 57 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 90 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6.9333 | 32 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.66666 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.1333 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.15 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.5 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.4999 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.2333 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.8 | 16 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6667 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.9166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7667 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.4 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.5833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.0833 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.66666 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.99999 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 30 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.5 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.3333 | 85 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 378.99 | 42.11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5299.2 | 576 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.99999 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.25 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5167 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.2667 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.6167 | 47 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 737.3333 | 28 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.05 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5333 | 19 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 24 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 10.8333 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.3666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.3333 | 74 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.3 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 334 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.86666 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.6166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.2833 | 29 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.0833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 154.1666 | 74 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 156.6833 | 79 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 57.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.55 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.65 | 13 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.9 | 18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.7333 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8333 | 17 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.0833 | 53 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.55 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.9667 | 14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.1 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3725.5168 | 66.31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.75 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.83332 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.9167 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.9333 | 29 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.4 | 24 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360.6333 | 31 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 924 | 84 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1341.6833 | 79 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 15 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.9 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.6666 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.5 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 362.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.55 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.6666 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.8 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 52 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.7 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1666 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.5333 | 52 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2257.4066 | 24.4 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 227.85 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 172.3166 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 52.5 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 97.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 34411.833 | 470 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2813.4999 | 255 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 417.9166 | 85 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 80.2333 | 166 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 59.5 | 30 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 73.6666 | 130 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 798.1333 | 73 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 109.8666 | 103 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.5 | 15 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1872 | 160 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 36 | 15 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 650 | 75 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 513.944 | 302.32 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1974 | 120 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1.3333 | 80 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 235.7333 | 52 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 750.5 | 57 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 424.9999 | 102 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0443 | Fuel oil (burner supply) pump drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 60.5 | 33 | 1 | 1 | 0443-Fuel oil (burner supply) pump drives | D1-Forced - Immediate | 100-Fossil-Steam
0444 | Fuel oil (forwarding/transfer) pump drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2200 | 800 | 1 | 1 | 0444-Fuel oil (forwarding/transfer) pump drives | U1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 569.9866 | 137.9 | 1 | 1 | 0450-Fuel oil heaters | SF-Startup Failure | 851-CC GT units
0450 | Fuel oil heaters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 413.3333 | 100 | 1 | 1 | 0450-Fuel oil heaters | D1-Forced - Immediate | 852-CC steam units
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 808.4832 | 271 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2097.4999 | 150 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3351.3665 | 271 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 113.25 | 45 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133.4 | 116 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5272.5 | 190 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.26 | 119.4 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 417.3166 | 49 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 476.5832 | 215 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1139.6666 | 260 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.5833 | 5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1644.1332 | 152 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 501.3333 | 235 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4156.6666 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 766.8 | 108 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 129.5666 | 169 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4206.807 | 115.89 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1519.2667 | 26 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 436.0833 | 209.32 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 718.75 | 15 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4783 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 176.4599 | 155.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 661.3333 | 160 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 914.85 | 321 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 632.3999 | 153 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 933.5333 | 44 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1019.1999 | 336 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1108.9832 | 253 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2310 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2369.3 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 142.5 | 190 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10619.3333 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 32.4 | 24 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 473.3332 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.3332 | 140 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 25.6 | 48 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 724.2 | 102 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2291.6666 | 110 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 460 | 120 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1089.9 | 155.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2166.6666 | 104 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6249.9999 | 300 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 300.99 | 114.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 441.1499 | 155.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 456.7665 | 193 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1025.2666 | 338 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 359.3333 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1545.4666 | 134 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 790.1665 | 431 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.25 | 15 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4011.1833 | 193 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2176 | 680 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 254.8333 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 534.8283 | 22.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 163.4 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 83.8499 | 117 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2346.448 | 50.57 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 68.4 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 83.6 | 114 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 75.9999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 81.6999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 87.3999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 98.7999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 163.4 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 87.3999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 171.938 | 50.57 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 41.7999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 150.0999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 110.9166 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2.64 | 1.76 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 60.914 | 15.96 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 414.936 | 8.16 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 361.9916 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 12.24 | 8.16 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 368.0416 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 109.9083 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 355.9416 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 367.0333 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 36.4873 | 9.56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 361.9916 | 60.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 89.496 | 1.76 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3405.5333 | 92 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 327.8533 | 53.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 97.3733 | 53.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 327.8533 | 53.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 324.28 | 53.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.25 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 476 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1100 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1302 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29337 | 770 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 920 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 476.8 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 533.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101504.75 | 635 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8837.5831 | 311 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6555.6665 | 554 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 399.1667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1008 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2112 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.6667 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 200.2 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.1667 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12903.81 | 557.4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 54.5095 | 26.59 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25 | 3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.5 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.75 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 899 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1008 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2617.3331 | 302 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20336.4 | 189 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.5 | 2 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.25 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149 | 4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 172.25 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160.6667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.4167 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 745 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 844 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32261.6666 | 260 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1220 | 48 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5243.3332 | 200 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.1667 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 271.95 | 259 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 764.1333 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58420.5 | 790 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24838.3331 | 700 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 2 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 375 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 379 | 4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1064 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2666.25 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 914.2 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1344 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6152.9666 | 197 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 12890.95 | 311 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 2 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.75 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146.6667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6291 | 270 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 10732.5 | 265 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | WECC | Off-Peak | 53343.9998 | 240 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 141.6666 | 170 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2110.2333 | 171.1 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 3384.9166 | 151 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 14102 | 132 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3337.6666 | 68 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 326.4292 | 7.85 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 961.05 | 29.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6495.65 | 93.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.1667 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37647.5 | 550 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 320.8333 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6493 | 302 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112665.5 | 97 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 210260.25 | 717 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48354.1663 | 550 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1023.75 | 175 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8155.9999 | 240 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 268.3666 | 83 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 351.1333 | 92 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2169.725 | 147.1 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17233.3333 | 220 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.5 | 6 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5323.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2095.5 | 127 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 414.18 | 10.62 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8408.5 | 134 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21522 | 510 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 950 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186.6667 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 348.9166 | 79 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 23.1999 | 87 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 56.3833 | 17 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 450.5 | 53 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66232.8328 | 770 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.3565 | 9.21 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2033.2 | 68 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2502.5 | 275 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2041 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 204.25 | 57 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 364.5 | 90 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 346.6666 | 160 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3404.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 567.7832 | 209 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 749.5833 | 175 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40209.9999 | 300 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1968 | 492 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16076.6665 | 280 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19385.333 | 560 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 23795.3332 | 140 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 24153.3332 | 200 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 750 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 19.1333 | 28 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 16693.8333 | 102.5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 102.6666 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 311.25 | 45 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 27.5 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 39.6666 | 28 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 586.6666 | 80 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 361.3333 | 80 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 261.5 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 146.2 | 51 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 860-Co-generator Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.6 | 18 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9856.25 | 475 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 10605.1 | 93 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1965.2333 | 107 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5406 | 510 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112581.715 | 42.1 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.2 | 86 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 768.3665 | 178 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 185.9375 | 17.85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74984.1661 | 790 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58731.3996 | 546 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 7501.0832 | 245 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230 | 50 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418 | 152 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 102 | 204 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10218.6666 | 160 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8527.5 | 225 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6554.1662 | 715 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 2639 | 7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 800-Miscellaneous
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 42675.15 | 419 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 125 | 125 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 1093.75 | 125 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Winter | 338.25 | 165 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2255.1499 | 159 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6112.75 | 49.9 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 143.5 | 70 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4391.6 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.03 | 4.31 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.09 | 4.11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 4.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.99 | 3.33 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.95 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.4666 | 67 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9270.7999 | 258 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43527.2332 | 257 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 4.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9628 | 830 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21592.3996 | 552 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 73766.9998 | 603 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11469.6333 | 223 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 20 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1164.8833 | 37 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 5 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 5.8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.03 | 5.37 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 263.5166 | 97 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 573.6166 | 127 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.99 | 2.33 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.96 | 8.44 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5747.5832 | 167 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10431.54 | 662.32 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2468.375 | 227.5 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4061 | 524 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 111.7999 | 129 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 7 | 1 | 4 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57 | 5.7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.03 | 4.61 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.9 | 39 | 1 | 1 | 0530-Other main steam system problems | D3-Forced - Postponed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.6 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1819.5706 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 11294.3798 | 296.7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 511.5867 | 24.4 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 9.45 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 829.8667 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2142.0332 | 358 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 12486.7333 | 157 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 16730 | 50 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 17020.1333 | 214 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 12407.1999 | 156 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 9197.5 | 50 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 27.8135 | 50.57 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 15.5166 | 37.24 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 45.0566 | 193.1 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 212.8 | 224 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 50570 | 650 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15950 | 638 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68863.6 | 136 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62973.9998 | 552 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3210 | 40 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5894.8333 | 113 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1225 | 50 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24904.3996 | 552 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 18159.8081 | 283.01 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 10173.6 | 216 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 756.6999 | 141 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Summer | 4864 | 152 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 9082 | 152 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 432.5 | 150 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2546 | 152 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 98.15 | 151 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Winter | 7813.2833 | 193 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 7505.0665 | 256 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 3818.6665 | 256 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 5538.6 | 153 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Summer | 106 | 106 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 4556.2333 | 106 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 3785.5 | 226 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Summer | 2158 | 120 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 4560.9666 | 154 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9779 | 55 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56597.2499 | 153 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4308.0332 | 259 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 837.4332 | 259 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2684.2198 | 522.9 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 7899.4 | 311 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3394.4166 | 55 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 7894.8 | 204 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 800-Miscellaneous
0541 | Cold reheat steam piping up to boiler | NULL | NULL | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 800 | Miscellaneous | TRE | Summer | 3157.8 | 114 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 800-Miscellaneous
0541 | Cold reheat steam piping up to boiler | NULL | NULL | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 800 | Miscellaneous | TRE | Summer | 14462.7999 | 114 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 800-Miscellaneous
0541 | Cold reheat steam piping up to boiler | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 25880.7999 | 204 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 800-Miscellaneous
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 9442.0332 | 242 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 3870.9 | 153 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6761.725 | 151.1 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 133.4716 | 151.1 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 2428.8 | 96 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 462.7999 | 267 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1515 | 45 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1857.75 | 45 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Winter | 274.4998 | 270 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 937.5 | 250 | 1 | 1 | 0550-Reheat steam relief/safety valves | D3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 782.6666 | 80 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 399.7499 | 117 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1946.8 | 93 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 344.5167 | 7 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1342.3667 | 7 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.5 | 75 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12045 | 33 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5039.75 | 95 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 591.25 | 75 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 54894.7998 | 699 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 190.8 | 8 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2142.4498 | 243 | 1 | 1 | 0550-Reheat steam relief/safety valves | U3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 1405.0499 | 171 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2298.9 | 237 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1516.8 | 237 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1333.2333 | 94 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 16929 | 90 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 1964.2665 | 232 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | WECC | Summer | 1682.1333 | 166 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 861-CoG GT units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 1185.6 | 117 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 862-CoG steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 180.183 | 569 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 464.25 | 619 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2431.9995 | 768 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 222.6499 | 219 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1733.55 | 273 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1627.5 | 310 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 688.2665 | 232 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 540.1 | 196.4 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Winter | 1985.9998 | 360 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1831.1998 | 252 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 172.9 | 91 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 730.3332 | 156.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 364.588 | 130.21 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Winter | 972 | 360 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Winter | 594.75 | 305 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4266.0566 | 151.1 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 9279.9999 | 174 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 83.875 | 152.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Winter | 385 | 140 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 984.6332 | 135.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Winter | 791.3499 | 199.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 49.9998 | 300 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 54.9999 | 300 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 60 | 300 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 384.664 | 137.38 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 82.5 | 150 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6862.3333 | 238 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 3896.2667 | 38 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Winter | 1240.2249 | 199.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 400.6333 | 119 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Winter | 389.025 | 199.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2890.5332 | 532 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27871.6662 | 700 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 868.4076 | 287.87 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 800-Miscellaneous
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 2789.6999 | 153 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 1557.5916 | 155.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 3332.8499 | 153 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Winter | 166.2056 | 262.43 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 2210.1332 | 256 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 1283.1 | 182 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 1659.1999 | 183 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 89.3 | 141 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1562.5999 | 156 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 16984.7999 | 378 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 641.55 | 91 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1180.6667 | 5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1415.8666 | 164 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | NPCC | Summer | 2232 | 144 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 3382.0999 | 186 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 2072.9049 | 204.9 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 1357.2499 | 183 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.75 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.2 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.9333 | 16 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64 | 32 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.5 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.45 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123.7333 | 58 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 492.1 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.7333 | 238 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 601.6667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.95 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.3 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 426.65 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 448.7 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1657.3331 | 565 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4011.469 | 97.13 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11900 | 595 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.65 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.45 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.6 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.55 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4989.833 | 455 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2552.6666 | 140 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.69999 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.05 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1640.9166 | 97 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5094 | 40 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204863.0661 | 838 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 462 | 23.1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.5 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1234.0999 | 258 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1342.4548 | 259.83 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 60502.8499 | 249 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.6 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.55 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.7 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.7 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.2 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 413.35 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 50.2667 | 29 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.85 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.7 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.05 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 504 | 21 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 735.84 | 10.08 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20914.6665 | 440 | 1 | 1 | 0570-Other reheat steam problems | U2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 103246.25 | 547 | 1 | 1 | 0570-Other reheat steam problems | U3-Forced - Postponed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 4488.4 | 229 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 2293.2 | 117 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 24313.2162 | 769 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 11382.8331 | 419 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 491.8666 | 119 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1207.9164 | 325 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 131.4 | 292 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 257.9498 | 231 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 264 | 176 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 23562 | 153 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Winter | 326.9999 | 180 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 297.336 | 228.72 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1157.3 | 85.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1149.5 | 190 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 98.1 | 54 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 151.5 | 10 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 18880.0332 | 468.1 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.9666 | 242 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 243.6667 | 10 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13452.3998 | 507 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 498.3333 | 20 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1360.3333 | 110 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19286.4 | 492 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1406 | 370 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8074.9995 | 750 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57308.333 | 575 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1610 | 280 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1063.4293 | 100.64 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 717.4998 | 246 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7774.8 | 627 | 1 | 1 | 0590-Desuperheater/attemperator valves | SF-Startup Failure | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3506.8666 | 164 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 114.3666 | 73 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 378 | 42 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.6167 | 23 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.0667 | 8 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 72.6665 | 52.53 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 674.5 | 190 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20349.95 | 691 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234.6667 | 22 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.75 | 275 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 334.9 | 51 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 885.9332 | 388 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3253.3498 | 369 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 282.2665 | 292 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29314.1331 | 416 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 540 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.65 | 19 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4158.4663 | 532 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85 | 75 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46860.3329 | 1330 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 12 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.1666 | 25 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1302.3999 | 192 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 228.8 | 96 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 900 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 715.6665 | 190 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39033.2662 | 634 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1563.2997 | 486 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52 | 26 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 379.9165 | 235 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 370.4999 | 117 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 191 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 497.34 | 552.6 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42677.0163 | 511 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9739.1665 | 650 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 8 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 13 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.3333 | 23 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 385.97 | 29.69 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 216 | 6 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66549.2332 | 511 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4315.1331 | 766 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17502.9163 | 595 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 45 | 15 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 800-Miscellaneous
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2175 | 29 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2277.95 | 87 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6665.0499 | 417 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | U2-Forced - Delayed | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1488 | 310 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.3 | 4.78 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18142.9 | 397 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.8 | 4.85 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1095 | 73 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 851 | 370 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 5 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 570.24 | 5.94 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114 | 14.25 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.16 | 6.77 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4290.24 | 6.56 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 215.04 | 5.12 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 618.75 | 3.75 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1487.5 | 175 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 831.3333 | 145 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 921.25 | 335 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225 | 225 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 335.8665 | 229 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.6167 | 17 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6397.1999 | 216 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10871.4661 | 832 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30109.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4519.1665 | 638 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16491.9997 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6017 | 547 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 570.3998 | 552 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.9167 | 23 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5141.5 | 226 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8385.7331 | 577 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19337.0665 | 416 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27322.75 | 455 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 22836 | 330 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2716.6662 | 652 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222145 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 93.2166 | 119 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20910 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.25 | 15 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.4 | 12 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8850 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 32662.5 | 750 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6707.9999 | 360 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21023.3331 | 742 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26961.1664 | 415 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10654.6666 | 122 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215600 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5870.033 | 458 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4959.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39511.5 | 742 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41387.5 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 19945.3332 | 280 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 650-Fluidized Bed
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2255 | 275 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 650-Fluidized Bed
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 78.1664 | 469 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 345.5832 | 319 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 116.7999 | 219 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1257.6665 | 539 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11289.6 | 6 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 264.9 | 3 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5543.1 | 9 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D2-Forced - Delayed | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1109.4 | 258 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 26397.7999 | 429 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 650-Fluidized Bed
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2349 | 290 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64687.9999 | 312 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 527.0665 | 268 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 650-Fluidized Bed
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1790.25 | 17.05 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2849.0332 | 254 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6561.25 | 45.25 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U2-Forced - Delayed | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 99 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 676.8332 | 310 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7534.9 | 151 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Summer | 625.0666 | 64 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U3-Forced - Postponed | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Winter | 63566.483 | 467 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 2470.9332 | 164 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 6487 | 130 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 567.8 | 51 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 860-Co-generator Block
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1150.5 | 295 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1481.3333 | 80 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.9167 | 5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2061.85 | 301 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11681.6 | 224 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10060.539 | 382.53 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12970.8332 | 275 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.2 | 12 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1312.2665 | 304 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 588.8 | 256 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4076.8331 | 401 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16129 | 635 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1862.5 | 745 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1209.9999 | 300 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 115 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40560 | 780 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14907.0832 | 475 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.25 | 5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3190.3332 | 340 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 810 | 270 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1591.9666 | 326 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 42.1667 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96891.6664 | 770 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 330.6666 | 320 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 250.0998 | 246 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 179.1725 | 275.65 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 146.8999 | 169.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 7580.95 | 107 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 542.1333 | 214 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 26.76 | 89.2 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 1107 | 180 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4317.5 | 150 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 9960.8665 | 187 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 126.5333 | 73 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 164.44 | 164.44 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 1901.65 | 73 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 265.95 | 197 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 5544.55 | 187 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 178 | 178 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 9675 | 180 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1867.0332 | 158 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 147.3332 | 170 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 12554.62 | 177.2 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 564.655 | 124.1 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 135 | 180 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Summer | 316.6666 | 200 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 80.5999 | 93 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 762.6666 | 130 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Winter | 4800 | 90 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1220.6616 | 103.3 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | RFC | Winter | 2668.5 | 90 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1380.5 | 251 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 93.6 | 54 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2247.4999 | 75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 128 | 128 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Summer | 614.2166 | 137 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1094.1 | 42 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Summer | 433.8332 | 137 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 123 | 123 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.25 | 5 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3124.1666 | 115 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1357.725 | 42.1 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.6 | 83 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.3 | 153 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.16 | 4.92 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315.462 | 64.38 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 497.0149 | 278.7 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | SF-Startup Failure | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 629.4833 | 211 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 3023.1666 | 170 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 417.8332 | 218 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 474 | 72 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 422.1666 | 170 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Winter | 3645.5 | 317 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 82.3333 | 95 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1424.9999 | 180 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 855 | 95 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Summer | 6 | 18 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.1833 | 127 | 1 | 1 | 0700-Blowdown system valves A | D3-Forced - Postponed | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6952 | 110 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 706.0598 | 246.3 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 489.7967 | 25.4 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 285.7983 | 13.1 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 110.2467 | 9.2 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 193.375 | 9.1 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21401.4 | 673 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 309.5917 | 9.7 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17032.6664 | 881 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 3024 | 112 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1822.3833 | 169 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1892.9999 | 180 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 7406.7498 | 645 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1777.3166 | 169 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 2882.9166 | 275 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 1015 | 175 | 1 | 1 | 0710-Blowdown system piping B | U3-Forced - Postponed | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 502.8999 | 141 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 1539 | 190 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 1529.5 | 190 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 4131 | 153 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 171.3149 | 218.7 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 1880.82 | 218.7 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 85.9316 | 109.7 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 872.115 | 109.7 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 597.4 | 103 | 1 | 1 | 0710-Blowdown system piping B | D3-Forced - Postponed | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 567 | 70 | 2 | 2 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5010 | 75 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Winter | 2592 | 96 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0720 | Blowdown system controls / instrumentation | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 2034.2811 | 287.87 | 1 | 1 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 800-Miscellaneous
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19239.7 | 842 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 8514.0519 | 115.89 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17858.15 | 619 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 4417.5 | 90 | 1 | 1 | 0730-Other blowdown system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 18154.1665 | 250 | 1 | 1 | 0730-Other blowdown system problems | U3-Forced - Postponed | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3438.266 | 964 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1177.9999 | 186 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4668.7833 | 113 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 464.49 | 238.2 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 5162.6666 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 272.1966 | 220.7 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2984.9166 | 49 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.4833 | 13 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 731.5 | 77 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 107.915 | 57.3 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2278 | 670 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.233 | 482 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1243.6666 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 22.7998 | 342 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 176.8664 | 379 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72138.7329 | 611 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6424.1665 | 593 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217.8 | 198 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 108989.3333 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 23104.95 | 201 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1601.2332 | 397 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112195.35 | 881 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1673.75 | 515 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19051.3329 | 680 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4212.75 | 615 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368 | 23 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 824.4832 | 191 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1709.45 | 179 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.7332 | 188 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2658.0832 | 191 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3828.6 | 108 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 918 | 9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 98 | 280 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5663.0166 | 59 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 107.6666 | 170 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1674 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68963.0665 | 259 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43225.3329 | 680 | 1 | 1 | 0740-Boiler recirculation pumps | U3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.5 | 11.4 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 376.6666 | 113 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3100.75 | 79 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 63.2665 | 292 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 122.4 | 18 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 650-Fluidized Bed
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 646.8 | 28 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 800-Miscellaneous
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 5401.7333 | 88 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 2330.5333 | 88 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 3002.2666 | 88 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 4380.2915 | 251.5 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 420.75 | 153 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 851-CC GT units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 302.5 | 110 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 637.0999 | 83.1 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6610.5 | 65 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 19440 | 450 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1078 | 49 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 322 | 46 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14214.7666 | 46 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34862.6333 | 74 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7828.1666 | 65 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10677.3332 | 280 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43081.8 | 118 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 19554.5666 | 61 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 241.5 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4224 | 48 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 44605 | 75 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368 | 46 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 968.9333 | 52 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1937.5 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 30982.8666 | 118 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.4833 | 7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 917 | 70 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37136.933 | 446 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40244.6665 | 530 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2035 | 370 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 654 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 5458.0663 | 589 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21122.5 | 595 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 40 | 32 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 650-Fluidized Bed
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 60.3366 | 157.4 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 850-Combined Cycle Block
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 755.6498 | 357 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 850-Combined Cycle Block
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3925 | 785 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2436.6664 | 860 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6674.8498 | 351 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5113.3333 | 50 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 928560 | 106 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 924.5166 | 326.3 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6072 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4903.5998 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9061.0666 | 176 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7240.3996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 14167.9996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 202.3996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 340.3996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 684 | 9 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1849.2 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4125 | 110 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 708.3998 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2005.5998 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 919.9999 | 276 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 850-Combined Cycle Block
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 286.6167 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.3333 | 76 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.4167 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6667 | 32 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2059.7499 | 224.7 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 121.6665 | 292 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1833 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1690.0663 | 502 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 203 | 20 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 25.3333 | 80 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.0667 | 32 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8505.8333 | 59 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 74 | 370 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.5333 | 76 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 128 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 20 | 100 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154.6667 | 32 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 696 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 85.5 | 342 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 214.5 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 65 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1578.4499 | 153 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 260 | 10 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9360 | 15 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 9311.6499 | 183 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 7650.72 | 151.2 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36999.0831 | 595 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 492 | 12 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3108.9832 | 167 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 247.5 | 10 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 10 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2773 | 118 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 35461.92 | 56.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2745.7099 | 359.7 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1782.3 | 182.8 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 158.7497 | 381 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 475.86 | 15.4 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 28564.6666 | 140 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 601.37 | 15.4 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 10144.155 | 56.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 7200.9333 | 106 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 44244.2 | 154 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1656 | 276 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 588.3 | 106 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1588.2333 | 106 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 4653.4 | 106 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 99 | 44 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 1152.2233 | 181.93 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | NPCC | Summer | 4071.1666 | 130 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1981.8666 | 128 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 781.4066 | 123.38 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 3129.7 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 2407.2 | 61.2 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 861-CoG GT units
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13218.0666 | 107 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 76867.2 | 188.4 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 21153.3 | 143.9 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 588.6 | 18 | 1 | 1 | 0780-Headers between tube bundles | U2-Forced - Delayed | 650-Fluidized Bed
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2218.05 | 93 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20849.4996 | 1110 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 783.624 | 16.48 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 805.2 | 72 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 852-CC steam units
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 4702.5 | 110 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.15 | 21 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1160 | 80 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2525.38 | 97.13 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4426 | 120 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35438 | 580 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12439.44 | 354.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 347.6667 | 20 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 26317.5 | 330 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3081 | 158 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16213.45 | 719 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1005.2333 | 106 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19681.65 | 717 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | WECC | Off-Peak | 3906.4533 | 33.92 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 435.96 | 21.6 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 345.72 | 20.1 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 418.295 | 31.1 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4257.994 | 50.57 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Winter | 3252.05 | 193 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 2236 | 172 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 6471.4 | 247 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3251.2 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 334.9333 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Winter | 2190.55 | 193 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | TRE | Summer | 1628.8 | 64 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2018 | Gas | GG | 852 | CC steam units | NPCC | Summer | 2863.2 | 144 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 852-CC steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | SERC | Summer | 1762.8 | 156 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 861-CoG GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1701.3329 | 638 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2566.95 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 535 | 107 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30559.3998 | 564 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 283.1 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28392.5 | 692.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 155.1333 | 26 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 291.7832 | 427 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 45.4997 | 390 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.4333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10171.3331 | 730 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.1667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 674.9997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 972 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1584 | 528 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.9563 | 9.13 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.1667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14127.6331 | 634 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1020 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 18673.0165 | 479 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.4 | 4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.75 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1095.4496 | 603 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.7499 | 225 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.2666 | 116 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11177.55 | 531 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.5667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 323.5333 | 92 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 885.5 | 253 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 569.4999 | 201 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3017.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315.9 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1679.8997 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3593.333 | 440 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.0833 | 107 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1254.7329 | 638 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 385.2499 | 201 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.9999 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1717.1 | 446 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 82.96 | 97.6 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 410 | 200 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 56.7333 | 92 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 21 | 90 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4887.75 | 665 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 2403.8666 | 88 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 5349.298 | 181.64 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 391.7653 | 91.82 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2220.5136 | 91.82 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 968.1499 | 201 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 60.1833 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 69.3 | 154 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 83.7333 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 27123.1999 | 312 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 8158.9998 | 492 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 24.3666 | 34 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 2117.9025 | 172.89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 60.1833 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 83.7333 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 24.4 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 34.4 | 48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3198 | 312 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 69.3 | 154 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 1535.1666 | 302 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 569.9999 | 225 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Summer | 1266.4666 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 26.7499 | 160.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 16.6 | 166 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 5423 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 442.2113 | 228.73 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3540.34 | 154.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 11122.4999 | 225 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 106.7499 | 183 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 1616.5 | 305 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 1426.8 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 28.6 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 195.4339 | 158.46 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 315 | 225 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 81.6666 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3268.35 | 243 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 739.5603 | 228.73 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 131.25 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2244.5332 | 152 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 139.5 | 186 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 44.6499 | 141 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 32.88 | 109.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 693.3331 | 320 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Winter | 92.0832 | 325 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 144 | 192 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 34.8333 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 663.3332 | 200 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 936.5166 | 83 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1027.0832 | 493 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 143 | 143 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 717.9333 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 31.2516 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 323 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 56.5833 | 97 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Winter | 57.3999 | 123 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 117.1667 | 38 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 355.3 | 51 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3.3333 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3.6667 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 1157.1 | 38 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Winter | 2073.9999 | 408 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 7909.3333 | 160 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 91.8333 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 44.3333 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 133.5 | 178 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 860 | Co-generator Block | MRO | Winter | 701.2499 | 225 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 2.9167 | 7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 530.5166 | 139 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 16157.3333 | 166 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 861 | CoG GT units | TRE | Winter | 87 | 174 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 95.1999 | 168 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | WECC | Summer | 797.4999 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 51.5666 | 91 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 46 | 92 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 594.5 | 123 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 8273.3333 | 85 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 689.1166 | 239 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 18.2 | 182 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 187.85 | 289 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 748.3164 | 761 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 287 | 574 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4172.4065 | 478.67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3024.8831 | 299 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 27.9166 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 37.9666 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 52.4999 | 157.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 78.2999 | 162 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 419.9999 | 180 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 643.5 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 1896.257 | 179.74 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Summer | 104.4 | 232 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2141.4366 | 179.45 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 27.9166 | 67 | 1 | 3 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Winter | 27.4999 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Winter | 4495.5966 | 230.15 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 194.4 | 72 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 56122.7175 | 228.73 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 1698.1193 | 165.94 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 514.5 | 245 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 2013.088 | 179.74 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 214.6666 | 92 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 409.5 | 105 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 4.4665 | 268 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 25.5733 | 109.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 278.125 | 133.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1285.3066 | 125.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | TRE | Winter | 97.5 | 325 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 66.5775 | 72.63 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1329.6165 | 126.03 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1485.8193 | 124.51 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1411.536 | 126.03 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 441.6893 | 228.46 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 68.4 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 300.3 | 92.4 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 58.8999 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 39.9 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 115.8999 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 114 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 121.5999 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2018 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 38 | 114 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3420.2833 | 163 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 33.655 | 38.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 46.8667 | 38 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 369.75 | 255 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | NPCC | Summer | 359.4498 | 237 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 5313.54 | 14.22 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 193.3749 | 127.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 196.475 | 135.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3483.2333 | 166 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | WECC | Summer | 337.5 | 225 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 204.85 | 51 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27319.95 | 531 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U2-Forced - Delayed | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 75536.9237 | 382.53 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 6681.5333 | 244 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 850-Combined Cycle Block
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4363.8782 | 265.82 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2358.9333 | 32 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83325 | 15 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12095.3666 | 218 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 995.8666 | 154 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.8333 | 110 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3180 | 120 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7267.5 | 342 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21105 | 300 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2356.9772 | 260.92 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2731.6667 | 44 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24088.5 | 10 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2988.3666 | 74 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 5785 | 130 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 278.6665 | 220 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 160298.6666 | 272 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15618.2666 | 164 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 30808.8 | 528 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.8067 | 35.18 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 235.053 | 40.18 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6940 | 40 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 720 | 160 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 211.6 | 92 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31761.2 | 586 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 247030.9333 | 112 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3358 | 120 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1799.2333 | 154 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 60095.25 | 435 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7862.25 | 15 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 109.6666 | 94 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 5800.0833 | 35 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 195.5 | 170 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5596.8 | 192 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 170059.4 | 268 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4383.0465 | 123.99 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1782.0833 | 235 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 44089.8999 | 237 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 346.1666 | 67 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 38955.1332 | 508 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 405 | 27 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0830 | Doors | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40890 | 705 | 1 | 1 | 0830-Doors | U3-Forced - Postponed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 50318.95 | 479 | 1 | 1 | 0830-Doors | U3-Forced - Postponed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 416.1666 | 110 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1866.8 | 104 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 48048.0165 | 229 | 1 | 1 | 0830-Doors | D2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4005.8332 | 230 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16348.3332 | 340 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5980.4932 | 178.7 | 1 | 1 | 0830-Doors | SF-Startup Failure | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4455 | 300 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1764.5299 | 421.8 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 249.0133 | 18.4 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 800-Miscellaneous
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 20172.5332 | 253 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 3545.115 | 177.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Summer | 318.5999 | 162 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Summer | 812.4999 | 150 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 9542.49 | 177.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 2.4955 | 4.83 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 754.3332 | 155 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Winter | 152.83 | 152.83 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3246.8749 | 187.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 905 | 150 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 2275.4416 | 120.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 774.9999 | 150 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 444.8 | 12.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5397 | 42 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7337 | 638 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8581.6665 | 190 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15060.5 | 105 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 28196.6666 | 200 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3448.5 | 190 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8521.8 | 42 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 610.05 | 14.7 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 41733.3332 | 200 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1035.5 | 6 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 197.8 | 6 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2953.5 | 6 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9096.9998 | 330 | 1 | 1 | 0847-Other expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 42420.6666 | 136 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2714.3875 | 114.29 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 49.9531 | 63.77 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36652 | 119 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1083.055 | 355.1 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6008.805 | 179.1 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 869.176 | 19.92 | 1 | 1 | 0850-Other internal or structural problems | U2-Forced - Delayed | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1760.1173 | 85.72 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 66.9585 | 63.77 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 48 | 16 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1023 | 22 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 676.5 | 22 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1760 | 22 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Oil | DI | 851 | CC GT units | SERC | Winter | 31.8166 | 83 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 56796.2666 | 87.2 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 861-CoG GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 6058.14 | 26.8 | 1 | 1 | 0850-Other internal or structural problems | U2-Forced - Delayed | 862-CoG steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 120.375 | 96.3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1197.415 | 21.3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 22048 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 277.2999 | 177 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36 | 4 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7516.8 | 192 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 179.275 | 21.3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 751.5 | 3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2060.9199 | 160.8 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165.85 | 93 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.2499 | 153 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522.7499 | 153 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 654.5499 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 325.5 | 93 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 126 | 63 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 75 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74.8 | 44 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 23.5166 | 83 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.6499 | 93 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 339.4666 | 127.3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 405.45 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.2 | 3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 685.9499 | 153 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14835.15 | 24.3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 82658.4 | 48 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 118.4167 | 29 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6.6 | 66 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.5999 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42453 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | RFC | Winter | 4256.2499 | 225 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 3520.9166 | 167 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 6020.35 | 167 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 21.82 | 32.73 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2740.8333 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 5.3333 | 8 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4686.5 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 3026.6666 | 160 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0856 | HP Drum relief/safety valves | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2018 | Gas | GG | 861 | CoG GT units | WECC | Summer | 8723 | 61 | 2 | 2 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 861-CoG GT units
0858 | LP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Summer | 11790 | 360 | 1 | 1 | 0858-LP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0858 | LP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 852 | CC steam units | MRO | Summer | 7245.1749 | 199.5 | 1 | 1 | 0858-LP Drum relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28722.8664 | 427 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2694.2825 | 63.77 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1030.9483 | 63.77 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3645.5183 | 63.77 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18757.4999 | 450 | 1 | 1 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2649.6435 | 63.77 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64192.3332 | 427 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1201.0016 | 63.77 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59300.383 | 497 | 1 | 1 | 0859-Tube external fins/membranes A | U3-Forced - Postponed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 7075.5 | 106 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 13232.8 | 68 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 850-Combined Cycle Block
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.8 | 38 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.9333 | 68 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 48 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.0333 | 13 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.4666 | 88 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.7 | 138 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.4667 | 23 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.4 | 88 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 153.825 | 29.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 63 | 6.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 132.275 | 14.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.6664 | 445 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83042.6666 | 80 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102.0743 | 43.13 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2637.6661 | 820 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.25 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.3333 | 20 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.7875 | 13.73 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 464.75 | 169 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.8682 | 139.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18677.0833 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.9999 | 420 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.5 | 15 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 376.6833 | 97 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.1003 | 19.13 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1517 | 820 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7918.4933 | 51.8 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1061.5 | 66 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.4142 | 11.95 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 806.3331 | 820 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.29167 | 0.5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 308 | 48 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5590.2012 | 330.13 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.0333 | 14.41 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.25 | 15 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.3 | 66 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 444 | 222 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.8 | 12 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.85 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.75 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 0.98333 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1330 | 95 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1712.1 | 39 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6039 | 180 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18 | 12 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 64.7833 | 13 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 844.3332 | 149 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72 | 9 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 307.7333 | 32 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1476.2999 | 126 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6675 | 125 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 530.5332 | 173 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.1667 | 50 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 229.7666 | 122 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1252.1 | 114 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.6666 | 40 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252 | 108 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1502.6665 | 196 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30 | 10 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17 | 60 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25 | 25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5344 | 320 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3724.6165 | 199 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2403.5 | 69 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 143.1166 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 177.374 | 20.31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 5.1572 | 3.19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 133.6 | 16.7 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 209.1 | 51 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1206.6666 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 656.6667 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2608.3333 | 250 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 134.3 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 0.5 | 2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.25 | 55 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2577.6666 | 74 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 67.1333 | 53 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 141.2967 | 22.31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1620.1 | 51 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1825 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564.6665 | 440 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3230.0332 | 254 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 652.5 | 145 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5670 | 270 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4848 | 320 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1665.3 | 42 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4310.9998 | 270 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1125 | 90 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 240.838 | 20.41 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1335.8333 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 356.25 | 285 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 37.7 | 29 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 444.4666 | 113 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134 | 67 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1924.9999 | 330 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2065.5 | 270 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 72.9 | 18 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 872.8833 | 83 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 120.6667 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 567.1953 | 32.66 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 151.6667 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 344 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 273.5832 | 245 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 63.3333 | 190 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 188.8333 | 103 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 139.3333 | 88 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 47.7 | 5.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 471.115 | 5.9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 1088.5 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 43.08 | 3.6 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Summer | 96.2667 | 19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 367.78 | 11.1 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1344 | 224 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 7302.4 | 448 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 35493.3 | 349 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2585.4166 | 85 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1082.4999 | 150 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 75 | 150 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21233 | 340 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.5833 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 964.3699 | 239.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5004 | 417 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40722 | 617 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256 | 128 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 140.3467 | 22.16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.6665 | 250 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6233.3332 | 275 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 23.1 | 6.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 6 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 19.3333 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24944.4 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57848.7 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62112.95 | 739 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 956 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69879.2707 | 291.67 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 341.25 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 471.7 | 10.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 54 | 24 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5994.6663 | 562 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8280.9998 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 591.5999 | 153 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1613.5 | 42 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5637.3332 | 224 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 152 | 38 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23195.9331 | 844 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 267.4333 | 142 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9650.6666 | 176 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2890.8832 | 349 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1057.7173 | 12.16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 42.7 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8261.5 | 533 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13427.5 | 410 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 323.2 | 404 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1824 | 190 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2245.3565 | 322.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27 | 3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 669.6499 | 177 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 366964.9832 | 277 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19132.6665 | 440 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33931.333 | 440 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10923.0332 | 277 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4261.3176 | 299.39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167153.1665 | 635 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2096.5 | 42 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 127.5 | 85 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 37.695 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 164.8 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 591.2833 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 56.7 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 413.1 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 603.5 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 35.75 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 130 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 283.7333 | 16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 112.455 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 159.4783 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 130.2 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 518.475 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 734.5 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1257 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 73.45 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 93.9783 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 169.1083 | 22.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 227.25 | 30.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1235.4 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 60.45 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 174.6833 | 22.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 381.3 | 12.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 633.245 | 12.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 152.75 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 527.8 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 71.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 261.225 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 42.1083 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 133 | 13.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 167.075 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 211.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 340.075 | 22.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 489.9 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 57.95 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 97.5 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 158.2 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1405.9117 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 55.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 66.5783 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 310.75 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 380.3117 | 17.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Summer | 142.75 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 90.585 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 110.7 | 12.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 116.5617 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 572.67 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 132.1667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 220.05 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 85.05 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 153.4167 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 40.61 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 100.45 | 12.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 152.75 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1168.1583 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 127.8 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 169.5 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 71.05 | 20.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 497.0117 | 20.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 556.7 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 52.2167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 123.6 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 148.7833 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 178.75 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 176.225 | 13.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 229.0033 | 10.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 652.4 | 23.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 234 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 356.85 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 380.4117 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 348.6 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 630.75 | 29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 356.25 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 304.5 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6110 | 200 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 622.5 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 803.8333 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2266 | 33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 425.6 | 24 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 627.5 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 798 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 197.9167 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 948 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 610.9333 | 29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 688.5 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 334.25 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 879.2 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2227.5 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 423.5 | 42 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.9999 | 120 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 877.5 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5453.85 | 353 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 34.1667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 404 | 404 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 387.5433 | 136.78 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 29.1667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4524.1663 | 610 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10652.9274 | 264.45 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13702.5 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.6666 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 24.1667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24216.4998 | 510 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 400.028 | 123.72 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 401.3166 | 121 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3420 | 300 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15529.9998 | 300 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 157.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 289.8697 | 1.51 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 40 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12879.1666 | 55 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46487.3328 | 824 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5945.4 | 108 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.75 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 630.2666 | 163 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 325.2666 | 164 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22742.8331 | 305 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 35.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31054.6498 | 531 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368.3332 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 840 | 70 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1029.3331 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.7 | 26 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4824.3331 | 820 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 60 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 339.8938 | 136.87 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 64 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 916.9326 | 236.12 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3402 | 141.75 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 299.6667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 348.75 | 31 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3386.25 | 45 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21069.9998 | 525 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10596.3 | 507 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 332.5 | 70 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163.1666 | 110 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 739.5 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4257.8332 | 433 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1984.22 | 141.73 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 194.205 | 129.47 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 41.6667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 54 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 833.3833 | 31 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 610 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 409.89 | 136.63 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 57.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198 | 220 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47246.983 | 437 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2915 | 220 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2742.6665 | 220 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2025.3166 | 137 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 337.5 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1341.6666 | 230 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 679.4998 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1464 | 244 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1147.5 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 294.9999 | 150 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2157.0832 | 155 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3200 | 200 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3354.6666 | 320 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.25 | 55 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1276.6666 | 200 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1683.4999 | 222 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2733.05 | 141 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6695.6 | 881 | 1 | 1 | 0894-Bottom ash piping and valves | SF-Startup Failure | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2033.9999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13028.0666 | 146 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 838.6333 | 139 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 677.3331 | 320 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 413.1 | 162 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3525 | 250 | 1 | 1 | 0895-Ashpit trouble | U2-Forced - Delayed | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 804.1665 | 250 | 1 | 1 | 0895-Ashpit trouble | SF-Startup Failure | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2600 | 80 | 2 | 2 | 0895-Ashpit trouble | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 394.8332 | 230 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1288.2 | 228 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2044 | 84 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2821.5 | 285 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15555 | 170 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3810.95 | 533 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28496.5332 | 544 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1058.0666 | 269 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3583.3998 | 228 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 175.305 | 9.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 497.55 | 31 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23783 | 340 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28792 | 590 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4271.4 | 339 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1028.0833 | 169 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2447.8333 | 190 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 836.9166 | 121 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2857.9999 | 120 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.0833 | 29 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 814.45 | 179 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2302 | 120 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2710 | 120 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 115 | 9.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 151.125 | 9.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 343.2217 | 21.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 239.8 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 259.9 | 9.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 183.625 | 11.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 318.2666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 781.9999 | 276 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3942 | 438 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1128.1365 | 316.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4609.2665 | 581 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 550.4 | 172 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1727 | 110 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 274.75 | 10.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 197.8 | 13.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2139.75 | 317 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.8333 | 65 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.8 | 53 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1046.3332 | 292 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32221.2477 | 815.04 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | SF-Startup Failure | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8880.4147 | 437.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55883.2996 | 606 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11917.98 | 816.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56332.8475 | 815.04 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3245.3666 | 167 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 751.8333 | 130 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1538.4999 | 255 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3974.1999 | 372 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4275.55 | 367 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6412.8665 | 428 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3107.9998 | 315 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 181.875 | 9.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 210.6 | 11.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 163.9 | 33 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4681.8664 | 388 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1979.25 | 435 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 768.9332 | 292 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 775.85 | 263 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1022.25 | 235 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2654.3 | 209 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 924.4999 | 258 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6752 | 844 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24811 | 860 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 675.5833 | 121 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4769 | 190 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3744.2 | 388 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5599.0665 | 392 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 460.8333 | 175 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 184.575 | 10.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3.3333 | 4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 582.1999 | 213 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7980 | 600 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | SF-Startup Failure | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30757.9994 | 840 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106482.8332 | 535 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 885.6 | 216 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1176.5 | 39 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1242.5 | 70 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3078 | 324 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.4 | 54 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3823.65 | 293 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 834.1666 | 175 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2858.7166 | 341 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5390.1332 | 493 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 136.2667 | 11.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 184.8 | 11.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 108.9 | 9.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1533.1333 | 244 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1960.1166 | 317 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 138.1683 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.8 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 108 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 825.1 | 74 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3739.3332 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16308.5 | 169 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146 | 73 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 908.5 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1690.0665 | 404 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2523.9664 | 406 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 54.4417 | 23.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1773.4665 | 283 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1557.05 | 209 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29513.4164 | 415 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56986.9999 | 420 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20780.4332 | 406 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.2 | 72 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1071.0665 | 232 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 134.7333 | 9.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 469 | 10.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 910.5832 | 245 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1185.9 | 177 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.3 | 126 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 37473.333 | 560 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3076.48 | 535.04 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.3332 | 158 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1766.6666 | 200 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1296.45 | 201 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26866.3038 | 808.82 | 1 | 1 | 0899-Bottom ash controls and instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1695.3663 | 562 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 596.9 | 254 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.8075 | 40.65 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 19.9833 | 11 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 368.1708 | 48.55 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1322.4516 | 184.1 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 344.955 | 18.3 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.6666 | 70 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 122364.6664 | 364 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5580 | 186 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23036.65 | 581 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49061.1332 | 364 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19851.282 | 141.24 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11701.1332 | 167 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 31 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 569.2166 | 119 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 360.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 393.4667 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 351 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 622.9167 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 68.25 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 523.0333 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1432.5 | 50 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 4200 | 200 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 90 | 45 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 3030 | 200 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1870.9166 | 65 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 15000 | 200 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 15156.6666 | 200 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65331.9332 | 364 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.8 | 43.16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.5 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4440 | 37 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4789.71 | 28.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8127.42 | 31.38 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.942 | 4.18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1735.3333 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.4667 | 44 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 65 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 362.5999 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1664 | 208 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3419.3333 | 115 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 12.5733 | 9.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 13.49 | 11.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 71.8833 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 18.1083 | 20.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 44.4 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 49.82 | 21.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1389.8333 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27199 | 590 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176609.9997 | 900 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.6 | 11.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1265.2 | 316.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1290 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1776 | 37 | 2 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.16 | 24.52 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3885 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.95 | 51 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 220.5 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1628 | 148 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 6.8 | 8.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 15.225 | 14.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.78 | 9.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 29.7733 | 11.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 199.155 | 21.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 48.75 | 19.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 101.0083 | 15.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 700 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23600 | 400 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 896 | 179.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1402.2 | 70.11 | 2 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10586.13 | 21.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22999.9998 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357 | 51 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 667 | 26.68 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1739.65 | 316.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5492.6666 | 140 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12439.68 | 27.28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 87 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 173.6 | 248 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.2333 | 67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8815.5832 | 295 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 20 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 22.8917 | 20.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 36.7033 | 18.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 93.8 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 4.25 | 8.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 48.8583 | 20.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 62.8933 | 21.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 223.3333 | 12.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 479.7 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 17.4767 | 10.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 33.9167 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 164.0667 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 142.2 | 27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1400 | 700 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6496.03 | 42.1 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.2 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 273 | 54.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 728.22 | 13.74 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1656 | 34.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1769.5832 | 155 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6533.3332 | 400 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10420 | 400 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15660 | 400 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 618.41 | 47.57 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3932.5 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11222.8332 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11416.4999 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 355.3333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 507 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1104 | 184 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 5.9333 | 8.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 148.925 | 11.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 5.4133 | 11.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 92.0917 | 21.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 172.8083 | 8.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23760 | 400 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 291.2 | 224 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 931.6666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1789.6666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10476.9 | 166.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 549.6833 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1107.05 | 316.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1795.5 | 171 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3809.9999 | 180 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 160 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 452 | 113 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1370.2666 | 344 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1399.7499 | 165 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 12.95 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 6.27 | 9.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 31 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 32.55 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 44.45 | 21 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 287 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1309 | 238 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3206.6667 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29907.4 | 458 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.75 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 552.5 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2997 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3457.2 | 28.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5388.3333 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7112.0966 | 166.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.9166 | 169 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364.5 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208 | 104 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 860.16 | 215.04 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 5.8583 | 9.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 10.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 36.9 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 12.0333 | 9.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 12.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13326.6666 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 452.97 | 64.71 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 535.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19977.9997 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352.6 | 164 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 534.75 | 69 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2053.5499 | 201 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176 | 88 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 8.55 | 9.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 62.92 | 24.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 437.2917 | 12.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 6.0083 | 10.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 8.28 | 9.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 114.2 | 12 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 26.27 | 22.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 66.78 | 21.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 68.7167 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 724.3666 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1200 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6012 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1600 | 800 | 1 | 2 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 496 | 248 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120118.545 | 816.3 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405 | 180 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 888.3333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3699 | 27.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5476 | 37 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.4 | 55.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17078.56 | 24.68 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1260.16 | 315.04 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2039.3333 | 38 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 21 | 14 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 108.0333 | 14 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 230.2367 | 23.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 6.825 | 10.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 17.7867 | 11.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5119.9998 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108 | 108 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348 | 348 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 4750.9167 | 47 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 66 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 39 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 427 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 400.8333 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6940 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 863.3333 | 28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 228 | 8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 10640 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 251.75 | 95 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 6.6 | 3.3 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 68142.0331 | 293 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1197 | 90 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1133.3333 | 100 | 1 | 1 | 0950-Other bed material system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0970 | Flue gas-solids separator | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 320 | 40 | 1 | 1 | 0970-Flue gas-solids separator | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 220 | 8.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 39.6 | 11 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 15.6 | 2 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 180 | 50 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 156 | 10.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 1806.7 | 8.9 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 419.75 | 15 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 62896.4166 | 251 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 4833.64 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 466.2 | 18 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1509.14 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 683.6066 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1552.77 | 24.3 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 38528.1 | 234 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1342.4066 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1390.3933 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1785.2667 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 501.6 | 18 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1095.93 | 24.3 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 864.36 | 10.29 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1054.4867 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 524.1 | 18 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 34216 | 235 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 522.3 | 18 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1 | 2 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6.7167 | 1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2.15 | 1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.2833 | 1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 9.7167 | 1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1129.3332 | 140 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1142.4 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1242 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2154.8 | 8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11179.9998 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 109.7999 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2008.242 | 36.58 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1416.6666 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 640.2 | 8.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 700 | 12.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 200 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 639.5833 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2040 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 235 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 177.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 248.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 347 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15239.5832 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 41800 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6443.4166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7314.6 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8163.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8494.7332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8735.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9707.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16854.4 | 458 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18283.9999 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21000.1178 | 264.93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25362.8 | 652 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32228.3664 | 662 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33345 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41960.1 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43761.2499 | 195 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46823.55 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86139.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296424.1331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5292.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6924.1665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14869.3332 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14886.7333 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15528.3333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16696.1166 | 263 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17406.6666 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18496 | 272 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22271.4165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22356.25 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31097.3332 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31931.6662 | 700 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39860.7499 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40545.8664 | 812 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56172 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79860.2 | 812 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3553.2 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6069.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7272.85 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14693.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28046.1996 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31362.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42262 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 49598.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120726.3664 | 881 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123113.6658 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149440.8995 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229092.5 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19663.35 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 25755.2164 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 26617.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24517.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23324.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 39022.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16665.7499 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11590 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 34262.1231 | 334.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 46717.4999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 4724.4166 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 10548.2999 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 11016 | 102 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 30103.5 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 67355 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 266755.3011 | 62.99 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2639.05 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 6204.1667 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15816.5332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85030.733 | 558.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12461.3499 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14033.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16190.5331 | 332 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50966.7498 | 717 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10026.1332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11534.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13490 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27666.6664 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44935.4664 | 824 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54926 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 36229.5996 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 69844.25 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.2666 | 28 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.5 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 208 | 208 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 708.75 | 22.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 777.6 | 16.2 | 2 | 2 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1641.334 | 36.76 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4787.5 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23102.4 | 192.52 | 2 | 2 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285.2 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 412.815 | 67.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 782.4 | 8.15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1277.8331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5465.72 | 9.14 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133.1235 | 46.71 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 188.7 | 222 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1339.5 | 28.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 78.3 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 447.3 | 14.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1079.85 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7392 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 6126.25 | 65 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 233.5667 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 337.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4924.125 | 145.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22634.6999 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29812.5 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765.0166 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1545.12 | 64.38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10462.55 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13533.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13832.0999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25591.4999 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29240.901 | 390.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29810.4332 | 502 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33746.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35719.45 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36339.2902 | 662.32 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41049.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66358.6662 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2487.9165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5970.4165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8328.9499 | 159 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9238.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13965 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21425.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22695.3329 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23511.0832 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23655.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25685 | 550 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38359.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39455.9331 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42755.3 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45432.9 | 639 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47866.25 | 745 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48461 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58653.8664 | 472 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60199.9995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81952.4998 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113114.3331 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6788.55 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7938 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8703.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9069.3331 | 760 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 9745.9666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13343.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23927.9233 | 120.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27536.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30336 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32472 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44021.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76526.6658 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 78235.6664 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78759.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178061.8661 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19229.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 35587.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 20745 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3224 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 13605.9332 | 508 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2838 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3974.5333 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22791.2599 | 421.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 25108.0781 | 334.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 47180.4665 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 98553 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 9312.4995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18292.1997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19002.1332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40200 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57213.1998 | 264 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2101.5666 | 67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 55247.75 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87926.6664 | 872 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63028.79 | 556.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55232.8496 | 531 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114151.7 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6832.6999 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 29898.7499 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 62175.2998 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 367.08 | 17.48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1693.965 | 35.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2898.9333 | 28 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7241.35 | 12.55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 632 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1671.6666 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 742.9 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1000.8333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 155.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 303.8708 | 58.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57352.5331 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5802.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9061.545 | 120.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9251.6665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22870.5829 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42134.85 | 529 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92340 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134008.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3080.2339 | 123.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6862.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7470.7666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10117.9165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10675 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14064.4166 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32647.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40503.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42746.95 | 311 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44356 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54654.8331 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3663 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5105.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6361.2 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28324.2663 | 568 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42797.4997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54529.9996 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 31737.2798 | 566.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 44441.55 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 442 | 51 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10199.5833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12979.1665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 16705.6666 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34636.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 36100 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 14003.8666 | 254 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 24840.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60300 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 111996.083 | 871 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226923.6 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12595.7332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16238.9332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14074.1332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8018.2666 | 154 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8700 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2541.5333 | 67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19472.2666 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 114935.8332 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 442.8 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 820.7833 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1867.36 | 42.44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3881.6666 | 137 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7791.6667 | 13.75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.6664 | 460 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 658.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1102.5 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5952 | 8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8604.1665 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1359.375 | 12.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 798 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 643.5 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 478.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 579.1667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14546.6664 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2779.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9686 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17012.9163 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20166.3332 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25805 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26254.3331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49165.644 | 141.24 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53092.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158610 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201448.3331 | 700 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8489.8666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9155.4165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10622.34 | 19.92 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25825.4997 | 405 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39748.8 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48367.9997 | 480 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53946.1662 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56740.8333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16921.3332 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25417.6 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30923 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38835.9997 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102278.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 115121.0661 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4200 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 44503.0828 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9225.2333 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12965.9999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 53340.5998 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 52656.7998 | 336 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2582.65 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2477.8833 | 67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3804 | 79.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16689.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19702.5 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85892.35 | 437 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16678.9332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17759.11 | 573.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39902.25 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 57767.3163 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5644.8 | 768 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 403317.7498 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 26093.3328 | 824 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8983.1998 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405.9 | 67.65 | 2 | 2 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.2 | 308 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 577.4996 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 692.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1932 | 161 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2816.8 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9649.9998 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 793.8 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1584 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3348.9227 | 11.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20976.9998 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5888.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 667.5333 | 13.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 3066.8 | 18.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 181.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5300 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1029.5833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3486.1475 | 74.57 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5753.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10256.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11677.5 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20339.7332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33522.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36072.0132 | 354.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40207.2831 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49928.4329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58899.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75965.1658 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76160 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76433.1495 | 723 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92430.7998 | 264 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102425.4329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 223044.8 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1964.4666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6660.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8475.6833 | 83 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8549.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8894.75 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9490.8333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10182.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10277.75 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12619.3332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13144.6 | 458 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13872.1332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18162.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21330.1999 | 276 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23781.9999 | 345 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30526.9165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34257.8332 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42832 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52620 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80360.48 | 336.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93151.5 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94500 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5668.1833 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6342.5 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19241.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22737.286 | 141.24 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25752.1832 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33249.9 | 822 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36379.9998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39184.1664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59658.6331 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77279.9998 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117753.3331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136659.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 39645 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1877.5166 | 104.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10067.9999 | 144 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23971.2033 | 99.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 75480.4281 | 334.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 8624.7 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 33168.75 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 556197.4333 | 71 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2470.6333 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 8223.75 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69105 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132667.8161 | 871 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4042.2499 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19067.3332 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44903.6 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11041.8664 | 752 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16099.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28583.6332 | 529 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51747.2831 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192276 | 872 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 51735.3331 | 568 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44539.1999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44931.9998 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69441.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21440.7229 | 390.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55626.75 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1179.5213 | 39.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1194 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1682.758 | 26.76 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2400 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3519.1 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2194.2 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3743.6 | 28 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3964.6 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5814.5832 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1240.8 | 9.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 882.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1391.5 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 696.9 | 10.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 1793.1 | 12.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 690.8333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 494.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 159.9 | 41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2724.05 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106232.9661 | 871 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1785 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.84997 | 51 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 912.9332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5716.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6966.6832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11601.55 | 331 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12800.7 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25217 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25257.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51216.3998 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58239.3997 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63179.0831 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77512.4991 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118725 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6195 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8468.8 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12215.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15343.9333 | 83 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16741.6 | 272 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19086.7498 | 459 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29399.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35150.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39087.1647 | 816.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56209.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56995.6662 | 652 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4306.5 | 638 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7137 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11682 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15334.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22316.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28125.283 | 479 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34144.5 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34208.5331 | 616 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45906.8496 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58963.3332 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 159931.7499 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36025.3331 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 29032.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 29137.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1140 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6209.6483 | 99.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 102206.95 | 547 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 80526.6 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 14278.7664 | 397 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19588.6497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15628.8 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20691.75 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40189.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 121052.8 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150162 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6810.4832 | 221 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60429.3997 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4469.1499 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38074.0828 | 815 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 175366.3998 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3518.6166 | 137 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212 | 53 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 558 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6829.277 | 9.23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10119.9999 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 645.3 | 54 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1680.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5167.6369 | 426.49 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1608.0833 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 170.24 | 12.16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 615.3 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 2299.4125 | 23.89 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 320 | 64 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 456.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 508.27 | 95.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2258.8999 | 147 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 247.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 620 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1113 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4125.3333 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 395.52 | 16.48 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6037.05 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9660.95 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9868.9997 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9949.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12515.1999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18593.9665 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28362.9998 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28990 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33308.4 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39831 | 710 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52989 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57174.4996 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 60452.4909 | 382.53 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5917.9165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12640 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24316.8 | 544 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25601.1 | 501 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38689.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47129.4998 | 570 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57700.4997 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 63114.6663 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73271.1663 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74412.4995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117899.9995 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3758.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4728.8832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5252.15 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5986.95 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7592.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11113.85 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15321.9662 | 673 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21328.6832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44692.9998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52368.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53278.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61905.7998 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 38610 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7078.1332 | 254 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 71997.6666 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 168589.2666 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2956.7999 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4093.8665 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6650 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 26859.675 | 334.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 27302 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 70343.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5161.4331 | 559 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27075 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 55447.5832 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 10395.9165 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2647.6667 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7248 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17944.5919 | 264.93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20853.75 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25500 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44292.3497 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91756.5 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7518.676 | 141.24 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15950 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37323.5 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54204.4998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 33056.9164 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 52360.1331 | 568 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4817.2999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6157.2999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12876.3 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.6666 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.7 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1549.1167 | 41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1878.1 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2220.12 | 52.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2343.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3168 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1713.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13359.5 | 694 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 230 | 5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 877.0167 | 10.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 768.6 | 12.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 592.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 51.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2450 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27248 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8875.4 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9525 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16229.3333 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18630 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21677.0499 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21883.9832 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40121.6331 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44849 | 860 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46745.9165 | 485 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50460 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158868.5 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1422 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11881.6 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17401.7498 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 17793.4049 | 153.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20228.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23068.5 | 455 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26332.5833 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26905.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 30239.7498 | 645 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56955.25 | 745 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101339.9991 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4042 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16068.8331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16276.1165 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25153.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30783 | 662 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 29302.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23047.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 166373.3328 | 734 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 46394.9981 | 334.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 156720 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2364.1 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5793.3333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16606.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25555.1663 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12859.7332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16191.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18576.25 | 275 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19072.2 | 717 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19385.3332 | 134 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28276.7997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31163.7999 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6071.991 | 123.54 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32447.25 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52151.6663 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 41246.2663 | 568 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32520.6 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3616.5999 | 156 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123756.5 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167354.8662 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2900 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 45860.2665 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 5539.1333 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7834.573 | 428.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 136.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1439 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | OG | 800 | Miscellaneous | RFC | Off-Peak | 425.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 549 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 722 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 503.5333 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 767.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 923.7666 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 834 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 835 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2145.3333 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 552.3 | 26.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 747.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 984 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | OG | 800 | Miscellaneous | RFC | Off-Peak | 1022.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 4368.4666 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1312.25 | 17.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 520.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1265.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1808.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1980.9183 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3451.25 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1900.5 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1779.75 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1424 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1295.6667 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3006.3 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 670.1333 | 16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 6149.25 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 702.5667 | 14 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 33756 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1256.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1275.5167 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1555.6833 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2999.3666 | 34 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 847.1667 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1777.9167 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2646.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 698.7 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 367.5 | 7 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2743.2333 | 47 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88456.6663 | 595 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2445.5667 | 47 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72 | 24 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 899.7333 | 28 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.35 | 9 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48401 | 580 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Off-Peak | 1097.6467 | 17.2 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 360.5 | 7 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26626.25 | 595 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 375.2 | 11.2 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 1738.8167 | 17 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 3011.1583 | 30.7 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4534.5666 | 166 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34495.6663 | 478 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25761.2997 | 387 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 148.75 | 7 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 626.5 | 7 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9048.75 | 75 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 187.2833 | 17 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 563 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 671.4 | 27 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2209.25 | 15 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 4123.9333 | 28 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 60883.5 | 45 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 290 | 20 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1822.65 | 29 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 652.5 | 45 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 879.9 | 14 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1417.8293 | 16.48 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27167.6662 | 745 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5702.7483 | 120.1 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40074.925 | 64.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3175.6333 | 47 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2124.5333 | 31 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2183.15 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2581.0833 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2753.4167 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41950 | 839 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 135.8 | 42 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 9870 | 75 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 123.255 | 4.98 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5551.2332 | 259 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 151.3 | 51 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2075.8333 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1514.1833 | 47 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1492.25 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 14874 | 268 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 520.2 | 15.3 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 527 | 31 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 622.425 | 19.3 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 690 | 30 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 783 | 27 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 772.3333 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Other | BM | 800 | Miscellaneous | SERC | Summer | 1064.65 | 19.9 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 693 | 27 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2938.1333 | 32 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 359.3333 | 14 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1193.6167 | 13 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.4 | 8.4 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10457.3332 | 155 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.9 | 58 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4214.6 | 39 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12132.5831 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26389.3333 | 80 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 367.0833 | 25 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41233.5 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11778 | 60 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3138.2 | 71 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99623.65 | 497 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2356.8 | 96 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9893.862 | 141.24 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51171.25 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43432.1997 | 486 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52855.5 | 334 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36202.5 | 75 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7739.5 | 30 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1274.25 | 45 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15220.1666 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8543.2 | 48 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3262.5 | 50 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34209.0831 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 10817.3332 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 215 | 50 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 407 | 110 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 19128.9998 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10066.4163 | 565 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42159.75 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7038.3333 | 50 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8953.3333 | 85 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2876.5 | 30 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16052.0831 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19664.5 | 335 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840 | 350 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1111.6666 | 290 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15352.5 | 690 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27897.0829 | 575 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50494.583 | 575 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26966.333 | 455 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62012.9998 | 630 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97291.5 | 1110 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 176.6666 | 100 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18840 | 200 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12725.1999 | 174 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40070.8329 | 590 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 911.4667 | 16 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9607.5 | 630 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15240 | 635 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28200 | 600 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21463 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39164.9999 | 450 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.25 | 15 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33866.6665 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 228657.45 | 1239 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 55872.95 | 427 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191466.7996 | 1239 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.2 | 6 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7680.75 | 231 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12458.2 | 167 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2832 | 80 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124201 | 770 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1389.6 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22680 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29456.9999 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47529.9996 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38218.6666 | 320 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70512 | 416 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15862 | 140 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27436.5 | 670 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71695.8664 | 728 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77939.6662 | 730 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 43147.9999 | 420 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33667.2 | 448 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36741.25 | 665 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4032.75 | 285 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40989.9996 | 600 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8048.7495 | 705 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14434 | 280 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7490.2366 | 120.1 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27375.6664 | 340 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22612.4999 | 405 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40189.9998 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5698.745 | 120.1 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34359.9996 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91819.9998 | 600 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 309606 | 1320 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2331.8333 | 85 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12098.3332 | 340 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 84512.6664 | 340 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24710.3831 | 661 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 569.3332 | 140 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7246.0333 | 120.1 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 30865.5 | 135 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78759.9996 | 600 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 27108.2 | 268 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 459.0667 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 505.218 | 15.69 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 12 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39984 | 192 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52971.75 | 585 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81408.0662 | 682 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146990.7466 | 336.8 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 64284.975 | 654.3 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2586.2 | 67 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5723.7499 | 285 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4346.578 | 274.81 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8234.2999 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31063.5496 | 651 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6308.5 | 66 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21049.6 | 598 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27661.6662 | 700 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33390 | 700 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7974.25 | 167 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22995 | 700 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92993.3329 | 650 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18115.2 | 136 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20170.5 | 339 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34635.6663 | 580 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 164.0333 | 37 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 543.6667 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11284.2666 | 149 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 996 | 12 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1865.6 | 53 | 1 | 1 | 1040-First superheater | D3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5550.555 | 65.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7195.8 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20318.9999 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41538 | 168 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57392.3995 | 815.04 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9742.7165 | 259 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10460.9999 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24241.6665 | 500 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65616.6665 | 620 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24179.9999 | 450 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 19366.4332 | 167 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110212.9 | 553 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5861.4998 | 285 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11016.2 | 446 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38932.9165 | 265 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 202237.5 | 750 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28332.5 | 105 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30449.6664 | 334 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31145.8331 | 598 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46153.7997 | 486 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119464.6664 | 680 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17028.8333 | 166 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31830 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32604 | 228 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38576.25 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21991.6665 | 500 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 54532.8499 | 411 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41291.1996 | 591 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1297.5833 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82994.733 | 479 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32561.2 | 812 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54859.8332 | 505 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17109.1666 | 245 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2071.4166 | 67 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115772.8 | 416 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 33055.8664 | 749 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 644.35 | 9.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 958.6667 | 16 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 137.5 | 75 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11565.5498 | 339 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13269.21 | 65.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13692.975 | 65.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9567 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47646.6662 | 700 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52144.75 | 415 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25525.5 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36887.265 | 65.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38760 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 78304.7723 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11643.75 | 135 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 42013.333 | 575 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18200.233 | 539 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 35557.3329 | 590 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36783.6 | 406 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 655.9667 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 297 | 10.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 390 | 13 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 646.6667 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1206.8666 | 42.1 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 50122.3663 | 598 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4628.75 | 69 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19101.4999 | 330 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125278.4 | 634 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1256.6667 | 20 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2581 | 145 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6639.4166 | 55 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6901.5666 | 197 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16265.7 | 106 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17854.8665 | 223 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125094.8328 | 830 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30272.8998 | 354 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16530.2166 | 167 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 183281.5005 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 77221.8331 | 577 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42830.9999 | 135 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1771.25 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1029 | 34.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2536.0416 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1095.1 | 23.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 25.5666 | 118 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 20345.6665 | 268 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2348.5 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1349.3932 | 19.01 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 968 | 88 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1229.35 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2381.2667 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5115.7666 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20991.75 | 195 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22825.9996 | 606 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97720.3331 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124888.3994 | 876 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143572.5 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9616.25 | 175 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9703.75 | 175 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18875 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26206.3331 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26723.5 | 290 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166069.9998 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 28002.5 | 575 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20567.7333 | 208 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32408.9498 | 651 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73470.8 | 568 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31485.6665 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43640.3329 | 590 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 92229.6662 | 658 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 48 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564 | 188 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 407 | 60 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 735.8 | 12 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 828 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3117.3332 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38528.9999 | 405 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39817 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215585.16 | 662.32 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6941.4666 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9630.1 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13181.9 | 193 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127458.3329 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9953.2 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62909 | 770 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125685 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2178.1333 | 64 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2972.255 | 42.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20765.7665 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75597 | 565 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30331.5 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 50474.6665 | 455 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2220.75 | 27 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 846.2 | 12 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 475 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 874 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 231.4666 | 248 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24082.5 | 475 | 1 | 1 | 1050-Second superheater | SF-Startup Failure | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17209.35 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37750 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84380.3331 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21949.6665 | 644 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97942.5 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2885 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3213.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4188.9166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7601.2832 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8266.5 | 198 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40455 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173853.1658 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 700 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 17000.97 | 332.7 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24937.6665 | 395 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11825.3332 | 245 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22350.75 | 255 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 38580 | 400 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 592 | 148 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1500 | 600 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1260 | 630 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 883.9667 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 436.8 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 2.254 | 4.83 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5477.6 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5524.9166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16885.15 | 199 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26149.4997 | 405 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32357.2329 | 638 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2730.7666 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29033.1332 | 271 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143122.4991 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146277.8329 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6588.15 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 56736.0997 | 393 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20221 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24334.4 | 134 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5073.75 | 55 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 302.7833 | 18.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 749.8333 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1188.7167 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6618.6664 | 340 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37584 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91848 | 712 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30861.3331 | 568 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36576 | 762 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4480 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6446.2 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14746.1 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41043.75 | 825 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1062 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1953 | 42 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 55725.6 | 749 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 18910.3999 | 334.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1932.4833 | 47 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10617.9665 | 458 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 211787.5994 | 876 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224 | 80 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 669 | 223 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 338.3332 | 140 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2173.5 | 27 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 515.25 | 15 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 658.3967 | 13.9 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 34.2 | 12 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 219.375 | 12.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 767.0667 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 8.55 | 19 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 315 | 12 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 157680 | 18 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 330.395 | 7.82 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14301.9083 | 120.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28197.6666 | 290 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43160 | 800 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106834.3464 | 700.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120939.6663 | 580 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6720.2666 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15477.5 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39018.3331 | 410 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54232.9691 | 662.32 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10735.3166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23108.1 | 394 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22042.8 | 351 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2258.9353 | 52.82 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37718.1665 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9983.75 | 245 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5425.55 | 221 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19465.4998 | 342 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 781.3667 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 878.3333 | 25 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 441 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5.4955 | 3.79 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 438.8323 | 7.82 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4008 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5616.7666 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16761 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21668.5 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23137.4997 | 450 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137794.15 | 709 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7373.3333 | 175 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129076.5 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51315.4163 | 535 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 74571.1998 | 528 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2025 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77698.5 | 554 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1588.5 | 90 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 11112.5 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 219.0666 | 248 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 354 | 118 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3686.6666 | 200 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2743.8017 | 7.9 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 471.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 610 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 49.3417 | 19.1 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 304.5833 | 12.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 393.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 15.0535 | 4.83 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9658.1666 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20156.9 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71585.6665 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165075.1658 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4139.6 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18077.6665 | 193 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156675 | 750 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18603.6662 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19024.9995 | 750 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191548.8665 | 638 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18758.333 | 500 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34549.6663 | 595 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11325 | 151 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46168 | 580 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31974 | 876 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 4830 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 25806 | 136 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 30912 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 6869.7332 | 268 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 167.75 | 61 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1226.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 12220.6666 | 115 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 22953.5999 | 216 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 25660.8 | 216 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 423.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 577.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 14104.75 | 115 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5078.1331 | 278 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 2519 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3711.8 | 268 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5977.1999 | 153 | 1 | 1 | 1055-External superheater link tubing | U3-Forced - Postponed | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62991.3662 | 721 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55856.4 | 712 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45212 | 712 | 1 | 1 | 1055-External superheater link tubing | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.4 | 12 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6270.58 | 39.94 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3535.1165 | 193 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 222.4999 | 267 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 877.0665 | 368 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5358.4999 | 210 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39558.4 | 448 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47629.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57741.6664 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30340.1329 | 626 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41056.3996 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48604.75 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57146.9498 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 25618.9999 | 411 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 27984 | 528 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12431.5 | 470 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14949 | 151 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39788 | 406 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25573.5 | 135 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 23262.5 | 250 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15995.8332 | 250 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11276.6498 | 231 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30850.3497 | 387 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46078.7997 | 387 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.6666 | 152 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3635.3332 | 280 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6719.5 | 44.5 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2607 | 66 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6556.5499 | 231 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12960 | 270 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37195.5998 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55149.4331 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77380.8 | 564 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78494.4 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29328.75 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39411 | 151 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48828.5662 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81704.6498 | 339 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87637.6665 | 644 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35728 | 770 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43127.0829 | 635 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7592.1998 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2585 | 66 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33707.7 | 387 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26979.6663 | 580 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3887 | 230 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 986.2739 | 94.23 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 173 | 10 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2062.5 | 66 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2841.3 | 66 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43378.2998 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69483 | 530 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14158.333 | 500 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20066 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70070.8331 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112190.05 | 511 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32768.6662 | 760 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8360 | 48 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15100 | 151 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16308 | 151 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14795.55 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 40908 | 168 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650.08 | 38.24 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2550.24 | 33.12 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4677.75 | 297 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5079.8 | 66 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31494.3999 | 192 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53452.8662 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105611.0829 | 635 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11645.9999 | 270 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19304 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22146.8866 | 178.7 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27400.4832 | 257 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38821.2998 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41772.4996 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56624.2664 | 472 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34626 | 580 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23967.9997 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37449.9997 | 840 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11923.8998 | 258 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39540.5831 | 565 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43475.8332 | 406 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32311.9994 | 840 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60282.8398 | 654.3 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 210 | 12 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858.6665 | 322 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 962.85 | 21 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7919.3332 | 280 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12219.9999 | 156 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21868.0664 | 662 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27378.2331 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51306.5 | 535 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84602.572 | 808.82 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27653.2 | 257 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52801.9998 | 510 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72115.1 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120748.3329 | 1300 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4034.8 | 262 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29182.8598 | 359.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35511.9998 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46016.6162 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70955.3664 | 662 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46737.25 | 595 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8520.0499 | 231 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34061.0663 | 568 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120229.3331 | 320 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31001.2253 | 264.93 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1162.2333 | 238 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 822.96 | 34.29 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1008.3333 | 220 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12285.3499 | 231 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21150.2449 | 264.93 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39175.2662 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45649.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88999.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10528.4082 | 178.7 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28215 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70842.05 | 257 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93936.2664 | 728 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14365.6329 | 638 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23442.3773 | 171.76 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33199.9998 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43138 | 120 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20471.7832 | 307 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27707.8 | 164 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19786.0828 | 749 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 381.9 | 201 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 210.4666 | 164 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 311.6665 | 220 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23157.0331 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86855.4 | 876 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40232.4998 | 231 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24360 | 600 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27261.3165 | 401 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9707.9165 | 575 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 32832.1 | 434 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2252.3166 | 67 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8503.7333 | 223 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15383.3332 | 250 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61041.0661 | 832 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27173.8497 | 387 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43978.9998 | 510 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48645.75 | 555 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7548.3832 | 197 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34376.5 | 492.5 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46752.6665 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53618.1332 | 334 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55732.8331 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100727.7332 | 253 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111236.6658 | 1300 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5606.3333 | 110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30604.3 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4237.2 | 66 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9211 | 151 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10157.2666 | 151 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62400 | 300 | 2 | 2 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7649.5832 | 275 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36093.9329 | 593 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4040.1 | 67 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300.2831 | 419 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 25012.4999 | 450 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127597.75 | 595 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21305.2497 | 459 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24805.5998 | 606 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1534.9999 | 150 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37054.5831 | 565 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13835.4665 | 307 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50624.3331 | 580 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16393.2998 | 231 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 60467.5163 | 523 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6471.8498 | 231 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59829.1664 | 415 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9362 | 151 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12309 | 330 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30771.4163 | 535 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31652.4998 | 330 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 195.9998 | 294 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43448.5 | 565 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 24629.9999 | 450 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25430.1328 | 752 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47918.1498 | 609 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30913.5 | 1110 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12796.7499 | 255 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17365.9665 | 307 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66045 | 1110 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 89497.333 | 560 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28517.3331 | 320 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24843.4999 | 330 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3348 | 93 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74502.9664 | 842 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37146.6664 | 800 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105875.4996 | 1110 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38440 | 800 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33621.9164 | 415 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41508.8331 | 658 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6701.3332 | 280 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117109.1329 | 1231 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40879.9994 | 876 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 36202.5 | 450 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22499.0415 | 492.5 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5388.6 | 42 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 565.5 | 15 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 30.8332 | 185 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 112 | 160 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39818.4 | 564 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43379.9663 | 613 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9943.2331 | 634 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22636.3329 | 590 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40748.083 | 485 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57982 | 530 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129328 | 472 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3080.5733 | 51.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1116 | 93 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 106521.1568 | 333.33 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6225.7499 | 135 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 979.0832 | 379 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1584.3333 | 49 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5962.6666 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29246.2915 | 492.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 866.3333 | 92 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37465.5173 | 264.93 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 148920 | 17 | 1 | 2 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 126 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 171 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 7008.3333 | 50 | 1 | 1 | 1080-Economizer | SF-Startup Failure | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33343.4831 | 299 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67466.74 | 493.9 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 48225 | 500 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 733.6 | 21 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25928.6665 | 380 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 984 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 386.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 40 | 120 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52962.3329 | 590 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125279 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9649.8166 | 167 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8808.55 | 51 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3926.365 | 53.7 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6124.3333 | 190 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 953.1333 | 58 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6876 | 135 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255111.9991 | 1320 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21400.3331 | 380 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 468.8083 | 10.1 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 362.825 | 11.5 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.84997 | 51 | 1 | 1 | 1080-Economizer | SF-Startup Failure | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13609.9998 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50986 | 530 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3218.6666 | 85 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5987.3332 | 280 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34059.5999 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 25966.6666 | 164 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2357.5 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 54703.0208 | 335.67 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 31152.5512 | 642.1 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 52.5 | 150 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 192.5 | 175 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.84663 | 50.8 | 1 | 1 | 1080-Economizer | SF-Startup Failure | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2207.2 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 109332.3331 | 610 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1932 | 42 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33786.3998 | 471 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39298.5 | 639 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6408.42 | 50.8 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1028.355 | 53.7 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2618.3333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4704 | 48 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32912.2499 | 315 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3676.3875 | 36.31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8606.25 | 405 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18135.5 | 415 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43723.3329 | 650 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3440.9999 | 180 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81973.9998 | 510 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3825.25 | 53.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 18483.8333 | 190 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 10952.7841 | 346.79 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2254.4 | 48 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 239.7 | 9.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 349.3333 | 16 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 415.8 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56661.45 | 499 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1641 | 60 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11819.8416 | 120.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22245.0831 | 395 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23899.9998 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9793.2666 | 71 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 16163.5829 | 605 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 104070.0999 | 177 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34904.5275 | 264.93 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7868 | 280 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9193.5 | 227 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 11266.5 | 111 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 4352.2916 | 32.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 2397.1667 | 38 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2385.3866 | 35.2 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 44370.75 | 335 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 582.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 587.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 848.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 543.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1210.5166 | 37 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 203.5833 | 35 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 550.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 554.1667 | 35 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 458.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 731 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 456.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1254 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 19810.75 | 363.5 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 2392.5 | 29 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1507 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 532 | 19 | 1 | 1 | 1080-Economizer | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2280 | 285 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 54838 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 476 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 14695.3332 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 23375.3332 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 15759.3332 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 337.5 | 225 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 927.5 | 265 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 26637.3332 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 631.5832 | 265 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3087.4999 | 285 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1260 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 294 | 120 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 45274.5 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2275 | 140 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 213.8196 | 121.03 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21586.82 | 57.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1439.5922 | 23.71 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 669639 | 174 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12067.9166 | 275 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2344.3666 | 53 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 396.25 | 75 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1520.8332 | 250 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6968.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8213.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57610 | 700 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33975.333 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 413238.3999 | 174 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3687.5 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35872.1665 | 265 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6290.1665 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34867 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.5 | 110 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 931.5 | 23 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1170.7 | 23 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8276.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9047.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39402.3497 | 507 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189175 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23601.1665 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41565.3332 | 260 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27199.1665 | 635 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31766.6999 | 441 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95361 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15365.5 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2677.5 | 15 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3164 | 113 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24604.3329 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260 | 200 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 266 | 280 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1958.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6278 | 86 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11704 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15722.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38972.6665 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55703 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5112.4898 | 332.7 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 14794.6665 | 380 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 50529.045 | 788.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 17440.6499 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 614.8332 | 155 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 322 | 11.5 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7740 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7925.5 | 110 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21361.5 | 606 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75074.4498 | 363 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10376.4953 | 175.18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30480 | 635 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10653.3332 | 200 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 39424.9998 | 300 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 11516.7998 | 566.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 7785.15 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14064.75 | 705 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11464.9998 | 300 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 886.2 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 85.5 | 342 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11774.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13190.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35657.2331 | 682 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60556.8 | 228 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77062.4995 | 1350 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 399854.8999 | 174 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7090.1665 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10793.0665 | 413 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28670.1999 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39007.85 | 413 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 22747.5 | 90 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11256.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22014.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665 | 75 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 48.6665 | 292 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 132.65 | 379 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1957.5 | 435 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1533.6 | 108 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6341.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7376.9999 | 180 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33299.5 | 611 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41463 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83489.25 | 195 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7101 | 263 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45532.5165 | 593 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31636 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 47010.8333 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 58028.85 | 209 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 33921.1999 | 411 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 6452.8666 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10710.6998 | 231 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67504.6663 | 520 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 383324.8999 | 174 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23568.5332 | 472 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7340 | 200 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 76837.5664 | 734 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16565 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 44063.3332 | 200 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 11412 | 240 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 16945.6 | 136 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 269.75 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 611.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2308.25 | 21 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 489 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1581.6666 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 468.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 843 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 276.6667 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 751 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1895 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 907.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 418.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 790.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 527.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 550 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 426.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 641 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 707.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1214.1333 | 16 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 2352.3833 | 31 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.4333 | 169 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 441.6666 | 100 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1113.75 | 45 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 192.405 | 114.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74660.3331 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149004.3329 | 1330 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32026 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25236.6662 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 2062.5 | 66 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 810.75 | 345 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5394.683 | 431 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 200 | 250 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 826.56 | 13.12 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1914.6666 | 320 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 1 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 6 | 4 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 540 | 27 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28274 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6359.25 | 183 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4859.15 | 157 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 565.8 | 276 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1300.8 | 271 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2391.1999 | 294 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11 | 11 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.5 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.04 | 136.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 182.88 | 114.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25463.65 | 839 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21000.6664 | 340 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5299.8 | 484 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5129.1332 | 379 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 167.6399 | 114.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9060 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1380 | 345 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1936.4 | 103 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 929.5 | 169 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.2 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 284.8999 | 111 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2756.5497 | 423 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5491 | 323 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21285 | 473 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 759.6666 | 215 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13088.0097 | 816.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6644 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 610 | 305 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1449 | 345 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1617 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.9333 | 7.45 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.9167 | 6.55 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 868 | 217 | 1 | 3 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31861 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7852 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 43503.8328 | 761 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.0833 | 31 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 687.5 | 275 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 15 | 3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 272.7416 | 142.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 313.5 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 574.9998 | 345 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1615.6666 | 148 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15280.4164 | 403 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164.7999 | 309 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 6 | 3 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 458.9998 | 324 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 583.3 | 307 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43081 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12759.5 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122102.6498 | 723 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 7.93 | 18.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 375.18 | 9.62 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 690 | 345 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1574.5 | 47 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 112.2333 | 14 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1710 | 7.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 152.1625 | 12.95 | 1 | 1 | 1105-Generating tubes | D3-Forced - Postponed | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 950.4 | 6.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 12906.96 | 6.6 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 552 | 23 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 9775 | 12.5 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 1943.1833 | 15.5 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 73.3333 | 20 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 565.8333 | 10 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5568.7023 | 22.22 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 432 | 18 | 1 | 2 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 864 | 18 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1296 | 18 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.9 | 18 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33549.93 | 816.3 | 1 | 1 | 1120-Convection pass wall | U1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 342 | 18 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39982.0777 | 34.22 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 508.8 | 84.8 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.92 | 8.86 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34813.3332 | 200 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37170 | 630 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.1 | 10.11 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2104.2166 | 50.2 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1751.6 | 5.8 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76508 | 496 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 485.7 | 18 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 446.1733 | 10.9 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1305.05 | 6.07 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2778.8666 | 114.2 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4713.3332 | 200 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109505.6665 | 497 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.5833 | 35 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D3-Forced - Postponed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1364.5332 | 301 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D3-Forced - Postponed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2806.6666 | 200 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.1667 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1387.5 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1607.5 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2147.2 | 16 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16030 | 35 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 257.0833 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 630.25 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3023.5 | 30 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3925.1667 | 11 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 545.25 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.0667 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.45 | 7 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2254.5 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5056.6667 | 20 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23081.6667 | 20 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1505.8333 | 65 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1608.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6451 | 60 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6521.6667 | 20 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1268 | 16 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1690 | 130 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2319.3 | 54 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4573.8333 | 65 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12309.3333 | 40 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 563.85 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3253.8 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11311.6666 | 55 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3160 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3313.75 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1992 | 240 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 815.25 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1801.25 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3357 | 60 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6135.75 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6198.75 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6282.9 | 26 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10185.2 | 24 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.6667 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 384.8833 | 7 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 574.25 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 763 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 922.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 965.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2536.5 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.5 | 26 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3074.25 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 255.8667 | 19 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1375.4 | 26 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 517.5 | 450 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 342.15 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 566.5833 | 65 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 413.4 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555 | 60 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 768.2667 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4063.5 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2913.75 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10877.5 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1807.4165 | 205 | 1 | 1 | 1140-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 662 | 40 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9427.5 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2892.5 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 754.4166 | 55 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1225 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1303.75 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7997 | 55 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 282 | 45 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.7 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1110.4165 | 205 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.8 | 26 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3310.75 | 85 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5188.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 779.9999 | 450 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1371.735 | 24.3 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 650-Fluidized Bed
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 25.9 | 111 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1579.7167 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1191.6664 | 325 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3392 | 848 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10616.6665 | 455 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.2 | 22 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.1667 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 219.25 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 316.6667 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 961.25 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1402.5 | 33 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1440 | 20 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10719.9997 | 804 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2083.0332 | 418 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2979.6998 | 498 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2541.4998 | 510 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3033.5498 | 507 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3134.9998 | 495 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2032.0666 | 326 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3242.9997 | 423 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4151.6665 | 530 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 535.8333 | 10 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 748.3333 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1476.3333 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2345.5833 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2351.2498 | 513 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2367.0832 | 475 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2429.4665 | 548 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2590.9332 | 448 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2636.1832 | 529 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2125.2666 | 284 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12361.0665 | 196 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.25 | 5 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 598.8167 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1364 | 31 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2010 | 402 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2248.25 | 391 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2534.4 | 352 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 480 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 529.75 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1920 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27334.9999 | 420 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2972.6665 | 392 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3465.2497 | 501 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2700 | 540 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156940 | 1330 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1364.9996 | 630 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1567.9999 | 147 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1584 | 33 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1783.4999 | 369 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3580.9165 | 443 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1631 | 105 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2499 | 17 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.6667 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 612.9167 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1643.8333 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4692.05 | 33 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1763.75 | 415 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10231.6665 | 175 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11412.65 | 199 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 604.9999 | 330 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2282.3665 | 458 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2943.7998 | 492 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3665.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 60 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 939.1666 | 230 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2706.6666 | 145 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 267.0833 | 64.1 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 558.6666 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 626.3333 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1824 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3154.4498 | 633 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3930.833 | 530 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4658.4998 | 462 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16131.8331 | 302 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108162.8328 | 830 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1039.9999 | 240 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1728 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2496.6498 | 501 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12037.4998 | 675 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 980.8333 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2064 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2411.9332 | 484 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3045.5165 | 509 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4135.3665 | 518 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1333.3332 | 250 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1907.0833 | 199 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3990 | 380 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.3333 | 10 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 736.0833 | 5 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2425 | 485 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2501.25 | 435 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2855.4164 | 445 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3021.7498 | 459 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3603.4832 | 469 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2406.9498 | 483 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2561.4332 | 514 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3739.5831 | 625 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 162.12 | 13.51 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64698.5 | 830 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23619.4286 | 309.02 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81539 | 335 | 1 | 1 | 1150-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 467.2332 | 131 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 989.45 | 33 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2448.3331 | 565 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2772 | 504 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2956.3998 | 456 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2974.4 | 416 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3727.5331 | 598 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6530.9332 | 152 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12380.9498 | 579 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.4667 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 733.75 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1411 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3648 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 563.63 | 47.1 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3379 | 545 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3968.9997 | 486 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2267.4165 | 455 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2901.95 | 457 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3081 | 474 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8566.6666 | 200 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2193.6 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 3592.05 | 33 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1339.5999 | 204 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 23.6667 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 30 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 175.9999 | 330 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 508.5 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5887.189 | 22.71 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 257.8333 | 130 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2240 | 280 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29692.6665 | 220 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37953.0665 | 644 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33831.156 | 390.66 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 856 | 107 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 884 | 34 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3828 | 174 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.99 | 4.57 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193.5833 | 23 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 978 | 163 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1117.9999 | 156 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 646.25 | 55 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 387.8333 | 130 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 673.2189 | 225.66 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 585.6 | 32 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2887.7333 | 91 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1469.8499 | 369 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1545.5332 | 388 | 1 | 2 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18 | 24 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 372 | 31 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1242.1333 | 34 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1872.45 | 171 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.99 | 2.33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.02 | 2.78 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 825.3333 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1344 | 168 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 83.8666 | 37 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.8333 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4983 | 151 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21466.0311 | 388.76 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 278.4 | 64 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 360 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2230.2 | 12 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46 | 4.6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2032.3333 | 52 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4630 | 60 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.3333 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 734.6667 | 29 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2077.8333 | 130 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.96 | 4.37 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 142 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1389.8332 | 310 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 534 | 24 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 694.5 | 30 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 591.6 | 51 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1696.8999 | 426 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49469.9329 | 644 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34986.4663 | 511 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 664.4167 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3591 | 171 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 875 | 175 | 1 | 2 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1084.2 | 23.4 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 387.8333 | 130 | 1 | 2 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112367.4 | 822 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64329.4163 | 595 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.0833 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.03 | 8.67 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.9 | 4.93 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4137.8166 | 203 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 496.4 | 34 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 510 | 34 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 594.6833 | 31 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4373.25 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15183 | 252 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.6667 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.1833 | 13 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 480 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 2.5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 960 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1155 | 165 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1899.5833 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2812.5 | 50 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.8333 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 79.3333 | 17 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 82.9667 | 19 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136.15 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 295 | 100 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 424.35 | 27 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 745.1167 | 19 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1588.6667 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1817.8333 | 130 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6199.2333 | 121 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1549.5165 | 389 | 1 | 2 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62563.4332 | 511 | 1 | 1 | 1160-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 227 | 20 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 767.5 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 9 | 1 | 4 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2638.768 | 29.04 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19502.9425 | 46.05 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1147.5833 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.5 | 5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 30 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 6 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38 | 9.5 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13826.7408 | 31.61 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.4999 | 150 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3996.25 | 15 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156.25 | 6.25 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.04 | 11.94 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16750 | 60 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.01 | 8.67 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.98 | 6.33 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75.35 | 33 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325.96 | 11.24 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 552 | 23 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 40466.8016 | 58.7 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 65.6166 | 31 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20198.2663 | 532 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16806.4165 | 235 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 941.3333 | 40 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 324 | 12 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 351 | 13 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6736.2 | 36 | 1 | 1 | 1180-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23370 | 492 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83 | 16.6 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12231.25 | 25 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 15530.6666 | 80 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 408 | 12 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 6877.0167 | 11 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5 | 35 | 1 | 1 | 1180-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 8.75 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 703.2 | 48 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1443.2333 | 29 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.6666 | 52 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1456 | 56 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 356.5524 | 168.45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 547.2 | 72 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 11788 | 42 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.9167 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.2 | 12 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.5 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1875 | 300 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25794.9999 | 300 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 390.8299 | 125.4 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 262.5 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6099.4165 | 265 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 635.8333 | 109 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6969.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 430.8 | 72 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1905 | 300 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.7002 | 9.83 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6681.424 | 163.36 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17591 | 49 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 485.8333 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1685 | 100 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4920 | 80 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 154.5 | 10.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 427.7499 | 177 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 490.2 | 114 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 590 | 118 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1403 | 61 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 336.6666 | 100 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1301.6666 | 100 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23194.9998 | 300 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 21429.65 | 47 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3319.25 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14648 | 48 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 25861.9664 | 427 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 108 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.9167 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1222.4332 | 182 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1630.1998 | 342 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.7 | 211 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 890.315 | 130.29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 343.1998 | 234 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3177.0833 | 125 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1283.4667 | 16 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4858.3333 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17144.05 | 427 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1801.15 | 163 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 207.4333 | 127 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 568.8 | 72 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 281.1596 | 92.69 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 459 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 11178.8 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1616.7667 | 41 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5017.25 | 47 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 679.9998 | 600 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 177 | 4 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2018 | Other | WD | 650 | Fluidized Bed | SERC | Winter | 5116.9999 | 102 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U1-Forced - Immediate | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 2426.4533 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1552.32 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 2423.52 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 3128.1066 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 5553.3866 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1913.12 | 35.2 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1560 | 30 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2575.9999 | 192 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 616.6832 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 908 | 227 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 585.75 | 11 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1060 | 265 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 376.6666 | 40 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 624.25 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1816 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1122 | 187 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.4 | 63 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1312.15 | 163 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 904.2166 | 227 | 1 | 3 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1242 | 207 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1362 | 227 | 1 | 6 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 422.675 | 8.7 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1276 | 319 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 367.5 | 30 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.3333 | 10 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2763.5 | 30 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 470.85 | 43 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1284.9999 | 300 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 908 | 227 | 1 | 4 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2618.0666 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 681 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 681 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 886.6667 | 16 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1580 | 316 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 427.5 | 50 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.9 | 18 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1123.4 | 164 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 454 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1362 | 227 | 1 | 5 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1396.05 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1475.5 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 869.2666 | 221 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 352.625 | 9.3 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1322.6666 | 155 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21964.25 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1629.4665 | 202 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1224.75 | 213 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1650 | 300 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 565.5 | 117 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1362 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2549.9666 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 908 | 227 | 1 | 3 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 1234.7833 | 13 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 335.7667 | 14 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 2303.6 | 12 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 286.2 | 12 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 362.5 | 15 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 8.2 | 8.2 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 146.75 | 15 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 383.4667 | 16 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 21996.3 | 18 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 650-Fluidized Bed
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.25 | 101 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 366 | 122 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6413.3332 | 200 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1300 | Water side fouling | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | OG | 850 | Combined Cycle Block | WECC | Summer | 4803.9998 | 240 | 1 | 1 | 1300-Water side fouling | U1-Forced - Immediate | 850-Combined Cycle Block
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2956.1165 | 193 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D2-Forced - Delayed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1878.5 | 289 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D3-Forced - Postponed | 100-Fossil-Steam
1320 | Tube supports/attachments | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10800.6664 | 340 | 1 | 1 | 1320-Tube supports/attachments | U1-Forced - Immediate | 100-Fossil-Steam
1320 | Tube supports/attachments | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40162.4999 | 162 | 1 | 1 | 1320-Tube supports/attachments | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84328 | 830 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255515 | 1300 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1110.6664 | 340 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15587.1 | 502 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 655.6332 | 221 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 10341.6 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3585 | 300 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 75.06 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1736.2666 | 68 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 225.4117 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 142.5 | 50 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370112.4 | 228 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 214273 | 97 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 142743.7 | 94 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D3-Forced - Postponed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30951.383 | 479 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 286.5717 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 412.2999 | 260.4 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 77075 | 25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 24912.1 | 111 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14.6667 | 11 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 32.0833 | 11 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 90.8367 | 11.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1448.5333 | 64 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35577.4996 | 525 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 122.1733 | 11.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3517.5 | 50 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10794.1666 | 50 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 23867.1 | 54 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 153.97 | 8.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 243.7133 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5671.2 | 13.9 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 489596.4 | 55.89 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 7540.1832 | 227 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 204.3333 | 10 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1633.6663 | 580 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14011.6662 | 700 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16992.0665 | 638 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8492.946 | 260.92 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2706.6663 | 580 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22947.1665 | 455 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | NULL | NULL | D1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | WECC | Off-Peak | 3879.1666 | 266 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 800-Miscellaneous
1360 | Boiler drains system | NULL | NULL | D1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | WECC | Winter | 4575.6 | 279 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 800-Miscellaneous
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1864 | 120 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1342.3666 | 154 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 284.76 | 90.4 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 18255.8499 | 159 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4277.5 | 145 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Summer | 7475.6499 | 159 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Winter | 4408.7166 | 161 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Summer | 735 | 140 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13756.1499 | 159 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Gas | GG | 851 | CC GT units | MRO | Summer | 7663.7166 | 163 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 446.25 | 85 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 8161.7666 | 98 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2802.5 | 95 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 8996.4 | 189 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 19451.25 | 225 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2018 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2836.6666 | 100 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2018 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 994.4999 | 183.6 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 861-CoG GT units
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.03 | 6.67 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 461.8999 | 186 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 465.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.5 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.8833 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.9833 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.5 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.8333 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 14548.1 | 49 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 24608 | 48 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56469 | 90 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1542.1333 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2583.9 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 73.5 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10824.2306 | 58.87 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2056.105 | 237.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.1167 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1239.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1770.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2554.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7053.75 | 95 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.7333 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.5833 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100.8333 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253.5 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.0667 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 407.9999 | 360 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1567.1333 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 120 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 123.5 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 375 | 150 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 411.45 | 211 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2397 | 141 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5158.8 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 48232.6833 | 119 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 38.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 593.75 | 95 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2135.6332 | 158 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3575.9165 | 235 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.6667 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.99 | 10.33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 157.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 398 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 625.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 916.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1644.9996 | 564 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1811.8333 | 70 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.85 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.25 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.5833 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.6667 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.25 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1264.4 | 87 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 216.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 291.6665 | 250 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 20.5 | 20.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 33.6933 | 13.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 350.0727 | 13.03 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 117 | 108 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 351.9 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 329 | 141 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 336.2332 | 131 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10965.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 49910.4667 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2747 | 134 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10810.7667 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 481.2499 | 165 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 467.0833 | 95 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1040.7498 | 345 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 167.3999 | 81 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 255.15 | 81 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.17 | 23.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 143 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 223.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 335.2333 | 178 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 346.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 373.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 380 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 555 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1296.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110620.9999 | 210 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.6167 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.9167 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.9333 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.9166 | 55 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.02 | 5.91 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.7833 | 41.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 183.6167 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310.4747 | 8.32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.9998 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6122.6664 | 328 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67505.3332 | 394 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.6 | 66 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 721.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 58.5 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6.3333 | 38 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 68 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4244.8 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6482.8 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 18198.3999 | 132 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1031.6666 | 100 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 207.8999 | 81 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 83.7 | 81 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 829.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16239.9999 | 210 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.6667 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.8333 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 332.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3492.9167 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 333.2 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4102.35 | 63 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41092.02 | 200.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 48.9667 | 11.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 63.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 52.9667 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 72.4 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 218.3332 | 131 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35483.8166 | 119 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 645.3331 | 320 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.4167 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 151.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 354.1332 | 128 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7986.333 | 485 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15598.3332 | 382 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 422.1 | 9.38 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 765.3332 | 140 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1949.3833 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9532.6666 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 92.2 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8624.55 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.8 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5637.53 | 115.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 48960.1667 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 123.2 | 77 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5687.4997 | 750 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 216.15 | 393 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 686.4 | 528 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.1333 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.2333 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 606 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 732.4165 | 235 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 972 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.1833 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206.9333 | 32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 304.4 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.6666 | 140 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1924.3332 | 460 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2533.3333 | 100 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26499 | 242 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1839358.5333 | 214 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 157.4 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 47.0833 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 90 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 176.12 | 125.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19940.9999 | 180 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 89.8999 | 93 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5932.4332 | 493 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1784.4998 | 249 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2607.6 | 492 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 458.3333 | 44 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 540.8166 | 37 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.9999 | 135 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 317 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2680 | 80 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12354.9999 | 210 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 302.5 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 606.9 | 119 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3725.3333 | 160 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 310.6666 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.7167 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 995.995 | 23.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1506.75 | 45 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2317.9599 | 200.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5625 | 450 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 211.6833 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 28.4 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 66.5 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 242.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1482.0666 | 172 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 407.225 | 232.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1819.9999 | 420 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 8 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2052 | 120 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22400 | 280 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2948 | 670 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 355.5 | 158 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | WECC | Summer | 74.1333 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 186.6666 | 80 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14 | 2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6974.3331 | 305 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 203.0497 | 393 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6688.4996 | 630 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.6666 | 115 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111 | 90 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 703 | 38 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 437.5 | 35 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1480 | 15 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1622.2663 | 529 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10911.2498 | 525 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136 | 85 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.8332 | 430 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.3 | 113 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.5 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 747 | 249 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.75 | 15 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 412.0833 | 115 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2556 | 15 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8522.4998 | 525 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 435.7333 | 76 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 484.6999 | 393 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29 | 145 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 537.0833 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567 | 135 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 657.5 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 31.1667 | 17 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14859.8319 | 180.96 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10674.2665 | 446 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16450 | 700 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 7447.2 | 107 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 171893.8999 | 411 | 1 | 1 | 1401-Forced draft fan dampers | U3-Forced - Postponed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1391.25 | 265 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.5 | 2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 153.55 | 83 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 290.5 | 83 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 30.9618 | 9.43 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 101.374 | 155.96 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1920.5 | 167 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 35 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 909.0666 | 112 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1877.083 | 425 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 874.5493 | 160.96 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 809.2 | 238 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4210.7733 | 56.8 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3792.2498 | 231 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2141.3 | 266 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.6 | 29 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 362.4999 | 150 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.7 | 306 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 948 | 80 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 51.3 | 81 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 24 | 8 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.88333 | 1 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | SERC | Summer | 96.1833 | 19.9 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 800-Miscellaneous
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 350.6043 | 130.66 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 32.9 | 94 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1807.6665 | 220 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1338.2499 | 159 | 1 | 1 | 1407-Forced draft fan lubrication system | D2-Forced - Delayed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 311.1 | 61 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1723.3332 | 200 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68522.6666 | 320 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4905.4166 | 305 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 10100 | 200 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61 | 12.2 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1177.5 | 45 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 170.4166 | 204.5 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 276.59 | 162.7 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8591.2665 | 431 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.2498 | 255 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1783.5 | 290 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14799.9999 | 300 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 63.6249 | 152.7 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 46363.7332 | 206 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1200 | 200 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37541.25 | 355 | 1 | 1 | 1407-Forced draft fan lubrication system | D3-Forced - Postponed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14672 | 160 | 1 | 1 | 1407-Forced draft fan lubrication system | SF-Startup Failure | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 37.92 | 37.92 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18481.6999 | 174 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.0833 | 205 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 527.65 | 61 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 907.9999 | 240 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2702.5 | 235 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9294.25 | 235 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179.6665 | 220 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 333.6666 | 308 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1707.6665 | 235 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6008.8 | 42 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17474.9999 | 180 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 47.9167 | 23 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 224.5833 | 175 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2552 | 220 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 221 | 20 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.3333 | 175 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90 | 180 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 317.9999 | 180 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52215.6664 | 409 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 672843.1332 | 454 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 125.0331 | 341 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1073 | 290 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6429.1498 | 351 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 156.3 | 18 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 3862 | 120 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 66028.4 | 184 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8428 | 172 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 29805.5333 | 119 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 160.65 | 81 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4493.4578 | 76.01 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 630 | 180 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5025.18 | 13.73 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30195 | 610 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35145 | 355 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 123.0499 | 321 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 278.1332 | 298 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2080.65 | 429 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3965.4998 | 330 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 98360.9733 | 206.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1088 | 680 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.9167 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.4166 | 77 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500.4999 | 210 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 886.6666 | 200 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3600 | 225 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12389.67 | 181.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3436.3333 | 130 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 83.8 | 209.5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 49.4 | 26 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 190 | 190 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2114.5833 | 175 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3904.9999 | 165 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1146.2332 | 502 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1885 | 260 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20109.0998 | 303 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 35.2 | 6 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 29082.3333 | 172 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 25463.1666 | 215 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 153838.52 | 206.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5580 | 450 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10289.9998 | 315 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3991.8996 | 627 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1173.3166 | 113 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4254.8332 | 245 | 1 | 1 | 1410-Forced draft fan motors | U2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22032.0831 | 275 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35096.5733 | 111.2 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 236.0166 | 119 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1413 | 18 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1793.75 | 175 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2511.96 | 76.12 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 468.9164 | 331 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 632.4998 | 330 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1444.9998 | 255 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64569.6 | 342 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 31428.9 | 47 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2444.1665 | 175 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21610.6 | 206.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 78.4 | 12 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53960 | 355 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.4165 | 205 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.5 | 165 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 27179.88 | 72.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 8280.6 | 37 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 12214.3998 | 528 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 144405.4999 | 138 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.7999 | 96 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325.3331 | 320 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1072.5 | 165 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1463.4333 | 86 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3285 | 180 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4950 | 225 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5167.5 | 195 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 907.9 | 42 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 320.4665 | 253 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 505.85 | 67 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 503.1999 | 222 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2383.5 | 227 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11452.3333 | 172 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16197.933 | 458 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 418.7 | 158 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 31.75 | 635 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 123 | 615 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2352 | 210 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 975 | 390 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2860 | 220 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 126.1333 | 86 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.4 | 109.4 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.6133 | 87.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1314.8 | 69.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3342.9333 | 64 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575.4833 | 14.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1802.6665 | 416 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 353.3432 | 149.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.4166 | 132.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1696.8 | 60.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379.5 | 45 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 25122.1332 | 256 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.8333 | 110 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1315.1666 | 65 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2767.9165 | 175 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 19858.8665 | 178 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3150 | 525 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24338.1997 | 876 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 13526.2999 | 138 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 724 | 90.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1020.0533 | 104.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075.2 | 89.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1803.7498 | 333 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 491.5333 | 202 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 947 | 94.7 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2228.65 | 53 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 184.5195 | 17.49 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340.4166 | 95 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.3333 | 80 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3453.3332 | 400 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 286 | 44 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 509.15 | 51 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414 | 18 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9928.5331 | 832 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 852 | 56.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1931.4 | 66.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10957.6664 | 355 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.6833 | 94.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2076.7 | 109.3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8570.1997 | 876 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 188.94 | 26.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 862-CoG steam units
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 263.5333 | 26.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 862-CoG steam units
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7307.45 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12124.4 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.56 | 75.9 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3212.15 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10191.5 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 65645.95 | 57 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34738.1 | 383 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 45 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1831.75 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8618.15 | 51 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1183.3332 | 200 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 15477 | 63 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.1 | 13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3333 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2252.4997 | 510 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2691.5 | 70 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 66 | 66 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5 | 5 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160.65 | 51 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3.1999 | 192 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 131.7333 | 26 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.8133 | 72.4 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3460.4998 | 270 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7778.6331 | 742 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.2833 | 13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.5 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 288.0283 | 80.38 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4193.4779 | 255.96 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 102.6666 | 28 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 7168.8 | 58 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2071 | 95 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 31.5 | 54 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285.75 | 381 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 60 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 100 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 279 | 45 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 15.1666 | 130 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 403.56 | 212.4 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 264.0333 | 178 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 519.1664 | 445 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.75 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232 | 29 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1710.6333 | 73 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 281.49 | 170.6 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 924.3 | 474 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 521.55 | 183 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.6667 | 8 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.75 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.5 | 22 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2033.9 | 473 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5.9999 | 90 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 914.1 | 277 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 437.5 | 250 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3851.25 | 325 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.047 | 35.66 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.1833 | 41 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 82.8 | 23 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 137.4999 | 150 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2249.5999 | 192 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 8 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2816.7999 | 336 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6454.6166 | 323 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 46.4 | 24 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1255.8 | 96.6 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1753.4998 | 315 | 1 | 1 | 1415-Forced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 3.2 | 3.2 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 650-Fluidized Bed
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 4.2 | 4.2 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 650-Fluidized Bed
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 264.0165 | 217 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 800-Miscellaneous
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 155.5165 | 217 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 451 | 41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 483.6667 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 536.9833 | 101 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 684 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.915 | 3.3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.9667 | 29 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287 | 42 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 586.4 | 48 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 597.7 | 43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 784.75 | 73 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 865.8 | 52 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2039 | 203.9 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 809.2666 | 122 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6009.0333 | 14 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 422.9166 | 203 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2135.3432 | 170.6 | 1 | 1 | 1420-Other forced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56027.8216 | 97.13 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 478.6666 | 80 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9523.7625 | 35.77 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.755 | 8.54 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 24 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.1667 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.25 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.8503 | 13.42 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 482.4 | 48 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 496.4333 | 53 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1280.4333 | 107 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 348.7998 | 327 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1364.6666 | 89 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 449.1667 | 35 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1646.6663 | 475 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4095.8233 | 80.6 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1.75 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 101.6 | 12 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2058.4 | 83 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23865.4663 | 568 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122367.6662 | 1265 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 78.6496 | 63.77 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 285.9021 | 63.77 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.4053 | 30.56 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1885.95 | 297 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3425.5258 | 41.23 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.95 | 39 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.4813 | 16.81 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.556 | 9.97 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.25 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 389.3 | 51 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 609.2333 | 49 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1462.5 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2054.6833 | 28.67 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61246.4996 | 630 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 871.7499 | 165 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1876 | 280 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 367.6166 | 161 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12 | 3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1068.75 | 475 | 1 | 1 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62060 | 580 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 89.1 | 81 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.6455 | 10.69 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 316.7666 | 43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 374.0833 | 67 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.25 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 526.6333 | 37 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 752.5 | 350 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 780.5 | 70 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 880.3666 | 77 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3969.5 | 467 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.8 | 7.8 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 410.4 | 108 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 560 | 200 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.85 | 39 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.7333 | 29 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.5 | 29 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.8 | 54 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 293.3667 | 13.54 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.6 | 47 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 566.25 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680.1665 | 530 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 688.1166 | 53 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1084.9333 | 79 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2807.25 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16039.32 | 37.71 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170 | 170 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 860.1666 | 130 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1484 | 112 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 251.7666 | 83 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12637.6666 | 155 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 26325 | 156 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.9833 | 29 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.1333 | 34 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.8 | 31 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.05 | 39 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.6245 | 14.13 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 347.3666 | 34 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382.6667 | 41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 578.55 | 63 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 797.3333 | 65 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1832.8 | 48 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2335 | 467 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 316 | 80 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 656.7498 | 555 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 14123.0832 | 155 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9.8333 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3921.3332 | 340 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3819.8331 | 410 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 980 | 35 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 324.2095 | 16.93 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376.55 | 51 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 378.7333 | 52 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.484 | 14.64 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555.3333 | 49 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 629.4393 | 18.94 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 789.3667 | 23.8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2191.86 | 19.44 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2308.75 | 75 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 193.3333 | 80 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.1667 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20633.9 | 6 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12537.1498 | 747 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2239.6166 | 83 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7539.4663 | 577 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 48102.9329 | 608 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 545 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3 | 21 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.832 | 17.14 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174 | 24 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341.2333 | 29 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 521.3332 | 170 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 523.6333 | 46 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 667.3333 | 52 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725.75 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 736.0833 | 55 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1483.25 | 85 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1831.2 | 48 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2102.6666 | 332 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9419.1166 | 83 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 14863.9167 | 35 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 49.9333 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 43027.2832 | 289 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 5 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 964.8 | 20.1 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 333.45 | 247 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.1666 | 170 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Summer | 126 | 14 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Summer | 334.95 | 21 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 5.4333 | 16.3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2104.5 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 902 | 328 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1420 | Other forced draft fan problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 75.0122 | 50.57 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 850-Combined Cycle Block
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.42 | 38.13 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 224.1 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 90 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D2-Forced - Delayed | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 42.3333 | 10 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 111.1 | 16.5 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 94.3667 | 19 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2674.9995 | 750 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 229.35 | 33 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 45.9 | 10.2 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 69 | 13.8 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 319.3 | 31 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 42.5 | 20.4 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 184.3 | 19 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131.9666 | 37 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 933.3333 | 32 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13821.3733 | 52.4 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 821.8666 | 67 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | U2-Forced - Delayed | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 8830.6 | 268 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | SF-Startup Failure | 650-Fluidized Bed
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 84.5 | 26 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 800-Miscellaneous
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 665 | 19 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123 | 123 | 1 | 1 | 1424-Secondary air fan/blower controls | D2-Forced - Delayed | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 540.4332 | 523 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4004.4 | 564 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 537.9 | 33 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 291 | 90 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11731.5 | 45 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1967.9566 | 135.1 | 1 | 1 | 1430-Air supply ducts from FD fan | U2-Forced - Delayed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1026.8666 | 146 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 243.3333 | 40 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10612.5 | 45 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 59385.6667 | 35 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1768.4667 | 41 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1326.4 | 6 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10482.3619 | 141.24 | 1 | 1 | 1430-Air supply ducts from FD fan | U2-Forced - Delayed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44285.4666 | 164 | 1 | 1 | 1430-Air supply ducts from FD fan | U3-Forced - Postponed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 43.75 | 35 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 767.2 | 7 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 360.2499 | 165 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20371.9999 | 330 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1087.1667 | 22 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1510.6 | 42 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 61.75 | 13 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 800-Miscellaneous
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 189.8 | 13 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 800-Miscellaneous
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 930.3 | 63 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10.5333 | 2 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 53.2 | 12 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57 | 6 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5766.4 | 51 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.85 | 3 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1.4667 | 4 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18 | 3 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 62.25 | 9 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 130.7167 | 11 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 193.6666 | 83 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 341.5999 | 84 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31.25 | 5 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 353.3 | 6 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.19999 | 12 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 32 | 4 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 44.5 | 6 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4.6667 | 7 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5.6 | 14 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8.5167 | 7 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36.9833 | 7 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 76 | 8 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 78 | 6 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 249.05 | 3 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9275 | 15 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5 | 3 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6.7166 | 31 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.2 | 6 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.6667 | 5 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 48.9 | 9 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1.2 | 12 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2.4 | 9 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18.75 | 3 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36.6 | 4 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37.75 | 5 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 46.6 | 12 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 99 | 22 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63 | 9 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 74.5 | 10 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7439.7166 | 43 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41212.8 | 162 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 948.6332 | 191 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25445.3331 | 416 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6618.6705 | 260.92 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4174.9998 | 300 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7014.9199 | 141.24 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 50 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.9 | 202 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1377.5999 | 288 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7728 | 46 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4650 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 5739.6666 | 335 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 3115.4999 | 90 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 9497.25 | 335 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 19693 | 419 | 1 | 1 | 1432-Air supply duct expansion joints | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 582.1667 | 35 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1045 | 100 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1174.5 | 45 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 759 | 115 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1698.6663 | 490 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.5 | 65 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 15022 | 259 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1286.5 | 31 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358.2 | 54 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1146.1666 | 65 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.5 | 115 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123 | 123 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45263.6799 | 200.4 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25 | 25 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 475 | 95 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 661.3 | 102 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 813 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1783.5 | 45 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2604.9 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3895.5 | 159 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.8833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 80 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1104.8333 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1200 | 100 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2002.8 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2497.5 | 18 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.3333 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 60 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 83.6333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 231.0667 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 262.4 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 515.2 | 21 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3157.7333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3393.8 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6525.6 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7137.3331 | 404 | 1 | 1 | 1450-Other air supply problems | SF-Startup Failure | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.06 | 133.8 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 834.3241 | 63.77 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 164.25 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 374.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3281.4 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.15 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.15 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.5833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 824.0228 | 17.09 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4252.75 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77 | 60 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 484.1333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 665 | 380 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 864.3 | 201 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 666.7366 | 143.9 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12980.7499 | 411 | 1 | 1 | 1450-Other air supply problems | U3-Forced - Postponed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1657.3333 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1699.8333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.35 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.3333 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132.3833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 430.5 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 721.8667 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3045.9 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.7333 | 44 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.0667 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3648 | 114 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 892.6 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 952.233 | 539 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 646.8773 | 66.46 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 900 | 750 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.2 | 18 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.7167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.6666 | 31 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.1166 | 53 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51.5666 | 119 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.3333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 527.2667 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 32.8 | 24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 63.75 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3822.1333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4452.6 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5757.8 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1357.1665 | 479 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2371.2 | 228 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.8333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.5 | 45 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.8333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.2 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280.5 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560 | 80 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 629.5333 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 309 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1425.6667 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2071.3333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2286 | 24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3773.6667 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 710.8832 | 221 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.5 | 58 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105.4166 | 55 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.5833 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.8833 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.6 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.5 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 933.8166 | 43 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1378.6666 | 55 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.2 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2731.3333 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 692.3 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 15610.1333 | 16 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14477.05 | 311 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.3 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 455.7 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 613.2 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2349.4667 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.8 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.3667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.15 | 39 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.5666 | 73 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145.0333 | 19 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.65 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.9333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.0333 | 43 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1209.576 | 9.09 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5139 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.8 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 151.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.4166 | 95 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 358.1333 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1512 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37 | 6 | 2 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2370.6 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 57.1666 | 49 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25255.9996 | 615 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.85 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 432 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3333 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 277.6228 | 28.09 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370.4167 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139.2 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 159 | 18 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 985.8333 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2703.0667 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2728 | 60 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2880 | 80 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4125.7667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19740 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1628.4 | 24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704.4165 | 395 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 584.0163 | 523 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 1967.9831 | 293 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 14.25 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 237.4331 | 419 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 904.4 | 119 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4189 | 59 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3402.25 | 439 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 984.3166 | 59 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 336.1164 | 469 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 388.4166 | 79 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2945.95 | 19 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.25 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189.9333 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 253.75 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 434.9167 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 502.8 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 551.3 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 598.6264 | 472.6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 786.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 862.3332 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 946.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 997.5 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1068.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1640 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2015 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2199.9998 | 480 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3915 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4773.75 | 335 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36365.3332 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143168.6667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.8333 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.25 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176.25 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 190 | 152 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.25 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 202.5 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 290 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328.2167 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 446.25 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484.1 | 103 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 494.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 517 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522.4 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 556.5 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 605 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 868.3 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 989.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1488.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1918 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 266 | 190 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1198.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1800 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3287.5 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56530.6666 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 139.2825 | 185.71 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 118.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.75 | 5 | 2 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 239.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20087.55 | 27 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.1666 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.3333 | 20 | 2 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 57 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.25 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 229.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 350.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 373.7499 | 195 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 588.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1251.25 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2398.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7636.8 | 43 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 327.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2048.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3113.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11760 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2303.4776 | 76.19 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.5666 | 107 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164042.9499 | 159 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1899.9997 | 750 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 11688.1665 | 190 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49878.55 | 839 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 420 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 503.3 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1048.3333 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1311 | 276 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1896.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3461.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6931.4999 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9538 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25480 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.5667 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.3332 | 206 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.1 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 636.1667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 662.9333 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 693.3333 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 701.55 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1101.7 | 479 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1607.9166 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1935 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3421.49 | 47.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3977.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6360.6666 | 290 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7309.9621 | 66.89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7475.48 | 44.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7711.3375 | 70.05 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18454.5 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35259 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 268280 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 127.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 231.1666 | 146 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 338.2667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 450 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 837.5 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5759.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32305 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 7209.9999 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 163968.45 | 303 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1986.1166 | 269 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4988.4683 | 148.54 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.0667 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 600 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1070.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1387.75 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1829.1666 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.8666 | 74 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 712.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 881.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1207.5 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4264.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5266.3332 | 427 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54572.7 | 546 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2768.9162 | 745 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32915.1331 | 652 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1849.1996 | 603 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4397.8665 | 434 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.05 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.35 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.3333 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.6 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 421.6 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 435.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1047 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2082.5 | 350 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2223 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2529.9332 | 277 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5882.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6116 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10374 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62451.5 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.3333 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.2 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.1667 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.05 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.7167 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.5833 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.15 | 227 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 425.6233 | 125.8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 481 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 811.9 | 138 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 933.3332 | 400 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1118.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1409.1 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2811.7833 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49.5 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 938.9167 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1405.9 | 102 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2448 | 306 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4011.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4824.9999 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22151.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133636.75 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 277995.865 | 418.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 76 | 12.16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1076.6666 | 323 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 12934.9998 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 7.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1488.8055 | 176.19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 11 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 19.935 | 0.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7464.3725 | 156.65 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 157.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3683.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8724 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.25 | 75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 164.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 211.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4680 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 78.2 | 69 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 365.5833 | 107 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 708.9332 | 409 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 200 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 91.6667 | 50 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 52700.6666 | 92 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 513.6667 | 20 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81933 | 620 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 159.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 263.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 320.5333 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 327.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424.5 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 790.8333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 813.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 943.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1068.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1342.6665 | 265 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1372.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2493.8666 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2591.66 | 40.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3589.2499 | 147 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7247.1666 | 59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8024.5 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9863.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10828.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13772.5 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37514.6666 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.0333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.3333 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.3333 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.15 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.8 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.8833 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 216 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 302.4999 | 165 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 377.6666 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.3332 | 143 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391.6667 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 662.5 | 106 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 920.8523 | 66.89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 925.4167 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1071 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1154.2 | 116 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1275 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28312 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43347.4133 | 24.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31.25 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143.1833 | 121 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.5 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 305.9 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 674.6999 | 117 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6862.4998 | 270 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10584.9999 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120000 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 254.4333 | 89.8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23177 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4617 | 190 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1.5 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.5 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.25 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 302.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 449.75 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 524.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4814.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22062.75 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.3 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.6666 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 330.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6318.3999 | 132 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 170.8498 | 603 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13682.55 | 471 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.5 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.45 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.8333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 129.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 213.0667 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 233 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312.0333 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 315.4666 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 335.4 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 366.9167 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 614.1333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 643.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300 | 520 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1338.1666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2933.7 | 46.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3593.3333 | 196 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3875 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4946.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7557.9166 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8014.9999 | 420 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12016.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28472.5 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5833 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.25 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.5 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.4 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.5 | 155 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.75 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.4 | 94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.5833 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328.8833 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 491.3333 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501.6666 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 612.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 721.4999 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 851.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 970 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 977.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1445.52 | 14.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2555 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3020.45 | 313 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3768.08 | 44.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30360.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 561.6 | 108 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 736.2499 | 285 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5444.5565 | 437.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28110 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46877.4999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94420.8333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 59613.3332 | 400 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 110.92 | 112.8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11804.9999 | 450 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.5 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322.2973 | 19.28 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 434.25 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 654 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1405.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 991.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1978.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25176.2 | 42 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 5097.111 | 76.19 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7219.4347 | 437.1 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.25 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 180.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 184 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240 | 30 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.6 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 405.3331 | 320 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 537.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 548.32 | 119.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1061.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2075 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2100 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2480 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2780.7333 | 106 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4055.1133 | 45.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8146.8 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.0833 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.5833 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.3 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93.7833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.9999 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 169.1666 | 145 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 202.5 | 45 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207 | 180 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264.3333 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 326.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 414.9499 | 129 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 502.25 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 521 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 592.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 601.0533 | 24.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 819.15 | 127 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 934.7333 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1221 | 44.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1521.6666 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2203.5167 | 19.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2340.25 | 115 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2402 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2710.0833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5301.1999 | 174 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6100 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6154.08 | 14.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9515 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10193.6 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72951.9998 | 480 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.1666 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3465.3333 | 226 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 13.3466 | 72.8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 926.1 | 378 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1092.5 | 115 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 111.435 | 13.11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335.5 | 55 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1312.395 | 30.45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2552.8499 | 81 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.5 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.75 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.8 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 320.25 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 698 | 60 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 902.5 | 190 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16656.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.9 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 359.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1222.8 | 72 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1294.8 | 72 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 31777.0833 | 175 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1192.7032 | 216.2 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6080.2 | 602 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.75 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 88.5 | 118 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.3 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.3333 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 266.0333 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 318.1667 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 386.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 609.5 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 674.6333 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 752.2666 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 784.4667 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1270 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1715 | 196 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2210.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3154.1667 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4687.6666 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5967.5 | 385 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7744 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18655.4 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21103.3333 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23042.25 | 285 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60628 | 184 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141143.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.6167 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.6667 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.75 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96 | 38.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140.3 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.1333 | 68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 198.3333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 228.15 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.2333 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 375 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 378.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 538 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630.0933 | 34.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 738.6666 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 739.7333 | 73 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1003 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1100.6666 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4183.5 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4496.6533 | 34.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6573.0573 | 66.89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39233.7 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.5 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 308 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428.497 | 27.38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1414 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 10230 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 40200 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122.25 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 923.6166 | 151 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 293 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8399.25 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.1666 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.8332 | 215 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 170.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 180 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1308 | 72 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 20400 | 850 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 169.8666 | 104 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8311.1 | 434 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 30.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.0667 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.6667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 226.9333 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 327.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 475.65 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 787.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 954.6167 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1095.3 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1464.8333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1912 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2834.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3579.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3798.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4740 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5154.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8453.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17280 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39979.7499 | 345 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 46816.0333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.4667 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 15 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.6333 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.6666 | 152 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.5 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.3333 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 120 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.6664 | 400 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 226.6 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 270 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 332.5 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.9 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 495 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495.8333 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 696.5 | 105 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 752 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 755.58 | 29.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 800 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1066.6666 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2473.9 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3764 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8303.2 | 21.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20135.244 | 140.12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.5 | 1.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.3667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 176 | 96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 176.8 | 272 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 536.92 | 173.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 637.5 | 102 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1099.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2900 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4029.6665 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97154.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3885 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 27247.1331 | 422 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3.63 | 3.63 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 335 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 426.4167 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 861.6666 | 55 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1680.5833 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6196.85 | 57 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.3333 | 20 | 2 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.4167 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 501.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 522.9167 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 535.4833 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16867.5 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1269.9 | 249 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1068.55 | 497 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1517.5496 | 603 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60228.35 | 427 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 718.065 | 24.3 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 98.2665 | 268 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 31.05 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1466.1333 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 706.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 58.2 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 97.85 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 977.5 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 88.45 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 29316.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 279 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1725 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 22.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8333 | 2 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27 | 2 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 251.3333 | 130 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2784 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.2 | 26 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1129.3333 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15189.6 | 144 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26596.9331 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222 | 8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 482.25 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1682.9999 | 270 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 900 | 60 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38949.1664 | 770 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566.4998 | 330 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.05 | 21 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.5 | 30 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 556 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30724.9999 | 375 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238 | 17 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 715.6667 | 19 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1029.9167 | 17 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2054.6667 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2213.0666 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.4 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.8333 | 7 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 356.5 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.25 | 15 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 680 | 15 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2114 | 280 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2193.3332 | 400 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.3333 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.5833 | 145 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.3333 | 14 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484.4667 | 26 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 906 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1687.5 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2166 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3266.6666 | 80 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.56664 | 34 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.65 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 704.1925 | 97.13 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 727.5 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7546 | 140 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.3558 | 8.65 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 216.58 | 12.74 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4386.5498 | 453 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13817.5328 | 812 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1369.4999 | 90 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88 | 11 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 272.55 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 361.1667 | 11 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 740 | 16 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1300 | 100 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2944 | 128 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104 | 8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.8667 | 16 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1644.7667 | 19 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12177.6 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80 | 5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.2 | 39 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 266.6667 | 8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 339 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 495.8616 | 73.1 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1105.5 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4080 | 15 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.5 | 5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8580 | 130 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13384 | 112 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.7833 | 139 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.8333 | 14 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 645 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.9526 | 66.46 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 498.1667 | 14 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 566 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 570 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 833 | 119 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.15 | 19 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.4 | 124 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 279.0664 | 364 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 529.5 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 992 | 24 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1789.3331 | 305 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7610.1664 | 770 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 445.2 | 106 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79.9999 | 120 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 188.3333 | 100 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 282.75 | 5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 11 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.9333 | 112 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91 | 21 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.9331 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.75 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 255 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 424.2 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1206.75 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.1667 | 2 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134.4 | 96 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432 | 16 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 279 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 586 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 765 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2751.8833 | 169 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7092 | 394 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11225.8666 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49438.5331 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.5833 | 95 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.5 | 6 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 285.75 | 9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 535.5 | 102 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1319.9997 | 990 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 13424.6666 | 104 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 650-Fluidized Bed
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 111.1 | 30.3 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 614.9998 | 369 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2646.6831 | 419 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 213.9 | 69 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95 | 95 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105 | 105 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.5166 | 197 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 295.1666 | 230 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90 | 100 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21854.9999 | 180 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 362.1035 | 231.13 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4910.625 | 218.25 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10911.2095 | 816.3 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.5 | 75 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1530 | 30 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1098.4999 | 195 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7244.6 | 356 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 271.3333 | 148 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2356.2 | 102 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5412 | 225.5 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.5 | 85 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 899 | 290 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 189.9999 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2489.9999 | 450 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3029.9999 | 450 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8108.3331 | 350 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 294.35 | 87 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 772.0333 | 53 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 806.833 | 515 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23344.5 | 395 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 639.1666 | 65 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4935 | 105 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76.2667 | 44 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 382.8 | 87 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1527.9166 | 95 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.4999 | 225 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 427.5 | 285 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 593.6666 | 260 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 668.1666 | 95 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 747.9998 | 240 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 921.3665 | 211 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12865 | 415 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3327.4999 | 75 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3430 | 98 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 337.5 | 250 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1211.25 | 285 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2674.4498 | 267 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2720 | 170 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75.8333 | 65 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.4666 | 71 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.3333 | 145 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515.6664 | 442 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2585.7332 | 451 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11426.9999 | 180 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2017.4933 | 216.16 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1663.3332 | 200 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18834 | 876 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.0723 | 5.18 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27872.083 | 443 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 240.8332 | 170 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 267 | 66.75 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1686.5331 | 278 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1088.1 | 120.9 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 650-Fluidized Bed
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2612.9 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1708 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112 | 4 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2275.05 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.19 | 47.4 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5746 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4698.3333 | 100 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1419.5499 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2089.9333 | 92 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9539.64 | 59.4 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2828.9499 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2608.0267 | 37.4 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 21.8333 | 10 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4458 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.8666 | 59 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.8333 | 10 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 550.9999 | 174 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2128 | 7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31284.1666 | 155 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69535.9998 | 318 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.7333 | 8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168.5833 | 17 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 719.5833 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3190 | 110 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26910 | 414 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.6333 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 141.3333 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 296 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 737.94 | 491.96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 879.6666 | 260 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1724.25 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5047.7166 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.7333 | 3.52 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.92 | 5.73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.471 | 24.21 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 210.33 | 11.07 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 380.4 | 15.85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.1 | 2.55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.72 | 4.62 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.848 | 14.56 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32 | 6.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.68 | 5.89 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.3 | 4.82 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.12 | 7.82 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 140.3 | 6.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 164.88 | 6.87 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 194.1333 | 20.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.315 | 3.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.4833 | 4.6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.4 | 3.84 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 28320 | 300 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138 | 120 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3325 | 140 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109430 | 310 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189792.5332 | 544 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.75 | 9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1759.24 | 170.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2085.2498 | 285 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6958.15 | 317 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7640 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8030.6666 | 317 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81073 | 380 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.6667 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 375.8333 | 82 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2391.6665 | 410 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7680.75 | 147 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 129.12 | 10.76 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.145 | 3.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.9 | 5.56 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 2.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.9 | 8.18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.88 | 5.61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.675 | 11.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 649.8 | 36 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 842.1665 | 310 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210.9 | 37 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 228.2332 | 167 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366 | 6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617.9999 | 180 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 767.25 | 135 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 979.2 | 102 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2035.3333 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.17 | 80.78 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144.4 | 152 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1035.9166 | 155 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2225 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4144.25 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5482.5 | 430 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6767.4 | 36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25057.5 | 390 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 331.3333 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 457.25 | 295 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3264.5666 | 119 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14260.1666 | 85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 88759.9999 | 120 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 323.15 | 14.05 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.8 | 6.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.752 | 4.92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.1417 | 13.42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.425 | 7.38 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.6825 | 5.61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 150.92 | 13.72 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.5402 | 8.47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230.0665 | 238 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9651.1665 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.25 | 15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45111.95 | 39 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48883.9 | 93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2443.25 | 337 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13060.8333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36410.9999 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.39 | 4.13 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.6 | 3.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.2 | 5.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.24 | 8.77 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.4 | 15.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 145.68 | 6.07 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 155.955 | 8.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 331.89 | 14.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.35 | 2.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 62.015 | 9.42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2167.1639 | 79.92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2590 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1359.7498 | 315 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 723.3333 | 31 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.5332 | 256 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1459.9999 | 120 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1300.8 | 36 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1514.6664 | 355 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1950.2 | 199 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 681.5 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.0833 | 5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.3332 | 164 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3016.8332 | 230 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11432.8 | 93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15777.444 | 79.47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33040.7 | 154 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38450 | 100 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 188.9333 | 52 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 218.75 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 266.4166 | 139 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 661.8499 | 93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1274.1666 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2872.8333 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3257.0664 | 394 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3846.5 | 105 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5360.9999 | 180 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29772 | 180 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5967.9 | 114 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.7 | 59.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192.48 | 32.08 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195.36 | 8.14 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.6383 | 4.27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 68.52 | 5.71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 186.48 | 23.31 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15.2123 | 9.71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 39821.25 | 75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 135250 | 250 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1357.633 | 482 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87683.9664 | 773 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44664.5831 | 275 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 106.5333 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.25 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.25 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 783.5333 | 73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1082.955 | 313.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5609.4499 | 93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6249.1833 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13856 | 128 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16629.4 | 73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30386.9998 | 315 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55634.5166 | 73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63611.2666 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186.75 | 135 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289.8499 | 93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1511.25 | 155 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7229.9999 | 180 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.5 | 30 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175.5 | 117 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1504.5 | 255 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5192.7 | 38 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.7 | 4.85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.9 | 5.58 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8542 | 6.17 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.2 | 9.6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.747 | 4.58 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.375 | 4.25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.2523 | 9.46 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.905 | 7.47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110.7975 | 8.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124.64 | 7.79 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3389.9065 | 231.13 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.2667 | 7.36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 26433.3332 | 325 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2757.0665 | 196 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4703.8332 | 167 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2018 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 435.5333 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | U3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.5 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 140 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 394.8 | 84 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7012.2 | 87 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8854.3333 | 202 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29340.7998 | 318 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175184.1666 | 145 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.9166 | 145 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.2667 | 7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 138.6666 | 52 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10938.4164 | 439 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.6667 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.3332 | 280 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 262 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4785.3333 | 97 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27552.7333 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.8 | 6.3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.865 | 27.54 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 369.74 | 26.41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.5625 | 4.95 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.35 | 12.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.1767 | 16.79 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.4 | 6.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.375 | 8.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.3905 | 26.49 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 210.24 | 8.76 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21.51 | 7.17 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1089.5832 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1348.2665 | 256 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4787.2 | 256 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.5 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1689.8 | 284 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.8332 | 245 | 1 | 1 | 1470-Induced draft fan motors and drives | SF-Startup Failure | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1552.3 | 361 | 1 | 1 | 1470-Induced draft fan motors and drives | SF-Startup Failure | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4009 | 422 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.75 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1333.6166 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2087.25 | 99 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9313 | 139 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17943.75 | 145 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55941.9 | 126 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 611.1 | 97 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 680.4166 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1394.9 | 377 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 235.3333 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.5 | 9.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.12 | 5.58 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.765 | 9.39 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 129.61 | 9.97 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 216.07 | 10.54 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 237.6647 | 12.94 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 266.4893 | 21.52 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1.7583 | 2.11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.3 | 4.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.0875 | 8.29 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.201 | 4.59 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.5528 | 7.93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.76 | 6.73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.52 | 6.96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110.72 | 6.92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 140.64 | 5.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.0547 | 2.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20.8575 | 9.27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 44.3333 | 95 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.359 | 64.38 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54436.25 | 275 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 112.75 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2931.75 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2843.7333 | 43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 536.25 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 627.2 | 56 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 7887.4 | 698 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1162.4999 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 157.5 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 281.6 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1279.0666 | 212 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1883.3333 | 100 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 328.5333 | 112 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 448.3999 | 177 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1541.3333 | 64 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 362.2913 | 587.5 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15 | 150 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2402.4999 | 150 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3566.5829 | 635 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6959.1665 | 175 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.0165 | 208.71 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3130.7724 | 336.04 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4800 | 100 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.85 | 67 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360 | 180 | 2 | 2 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 160 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 796.95 | 99 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 910 | 280 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4512.6665 | 280 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3409.0665 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1061.6666 | 260 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1120 | 140 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9999.1139 | 432.55 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.0666 | 242 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.619 | 125.18 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1533.9999 | 195 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1172 | 293 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33122.6666 | 160 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7.65 | 17 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.9999 | 210 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.1664 | 385 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7639.6666 | 215 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1567.5 | 95 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 343.875 | 327.5 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 517.7832 | 132.2 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 772.2665 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2594.1332 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5849.6 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 299.0832 | 185 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 739.26 | 133.2 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4633.3333 | 50 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7702.5332 | 328 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 219.9999 | 165 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2145.8333 | 125 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2403.0159 | 434.28 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 187.7332 | 352 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1037.0832 | 475 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3313.8329 | 590 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 821.9749 | 161.7 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 830.8666 | 121 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1096.0666 | 164 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.4 | 328 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10470.85 | 181 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1382.3332 | 286 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 649.1665 | 190 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4963.5829 | 635 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 622.8203 | 63.77 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 892.1665 | 530 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.8 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.8665 | 256 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.6665 | 250 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143.3332 | 200 | 2 | 2 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 830.25 | 205 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2754.1665 | 250 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8820.4666 | 164 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 280 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48.5333 | 56 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 861.9226 | 190.13 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1676.1 | 453 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1896.4 | 431 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365.4 | 203 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140 | 200 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200.7499 | 165 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.8 | 328 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143.65 | 221 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 617.7332 | 328 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 676 | 260 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1820 | 455 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7106.6666 | 200 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 650 | 20 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10042.4833 | 181 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34 | 340 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.05 | 401 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2370.6665 | 635 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 557.3333 | 55 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 72.5763 | 18.22 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1611.3 | 246 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 471.7499 | 382.5 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4144.9133 | 76.1 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 153.8133 | 16.48 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1061.9999 | 216 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37518.8666 | 52 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2663.5 | 76.1 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1033.8125 | 17.85 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3923.3333 | 107 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 806.6666 | 80 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.6666 | 40 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105.45 | 111 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 260.8333 | 25 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 743.0498 | 231 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1176 | 294 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1526.6833 | 139 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7989.5832 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115428.1665 | 190 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.3333 | 100 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.3332 | 140 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 387 | 129 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1223.0999 | 243 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7507.75 | 295 | 1 | 1 | 1475-Induced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4134 | 530 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10290 | 600 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 466.96 | 62.4 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.5 | 85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504 | 252 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 588.2998 | 333 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 588.7666 | 34 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5976.4666 | 314 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.5 | 30 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.3 | 311 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 669.6667 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 324.2665 | 256 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 393.8332 | 170 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3569.75 | 131 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11900.6831 | 293 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 322.5332 | 328 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2492.7999 | 96 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 543.95 | 253 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 166.8 | 72 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 867.2998 | 531 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.55 | 111 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 477.2999 | 333 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4130 | 590 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20494.0666 | 221 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.5333 | 14 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1150.8665 | 283 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3874.2999 | 318 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 163.3332 | 140 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 201.25 | 175 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 260.2665 | 256 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 288.5 | 57.7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23343.3332 | 149 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 205 | 75 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.9966 | 66.46 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.5833 | 85 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 882.45 | 477 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 784.5 | 523 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9222 | 530 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1506.6666 | 80 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3591.25 | 325 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 709.3333 | 112 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.6833 | 49 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.8833 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 120.2666 | 82 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 152.95 | 57 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 183.5166 | 91 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 191.1333 | 47 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.7998 | 306 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2172.9331 | 344 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 399.3581 | 281.9 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2222.5 | 127 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6724.6666 | 131 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 714.9998 | 330 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 775.8833 | 13 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 222.5 | 30 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 446.9665 | 253 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3286 | 310 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5112.0996 | 654 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 435.1999 | 102 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 630.85 | 111 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1180 | 590 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8150 | 100 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 957.4832 | 283 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2593.5 | 273 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21.3332 | 256 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1479.25 | 97 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 965.8333 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 237.9333 | 43 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8665 | 253 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.0999 | 102 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76 | 40 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.4861 | 85.51 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1125 | 450 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2431 | 130 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3403.1666 | 70 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7949.6 | 304 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2221.6833 | 139 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3973.0666 | 94 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1924.2665 | 256 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1067.2 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3.3 | 1 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1512 | 270 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8962.3329 | 644 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 538.9 | 102 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 318.9166 | 43 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301.3333 | 40 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 710.6 | 76 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2504.6665 | 578 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214.5667 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285 | 300 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2384.3332 | 230 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 108.35 | 33 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.9999 | 210 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395.1166 | 151 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.94 | 13.71 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 322.2833 | 61 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 130 | 39 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 918.75 | 245 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4816.6666 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184.8 | 66 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 245.1 | 38 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.9164 | 385 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 642.8331 | 290 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1061.9499 | 201 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2803.5 | 267 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7470.4666 | 167 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 205.6 | 257 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 55.3667 | 11 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 50 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4633.4165 | 455 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 64.74 | 4.98 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 164.3333 | 20 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.2666 | 64 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6503.9998 | 360 | 1 | 1 | 1476-Induced draft fan speed changer | D2-Forced - Delayed | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2124 | 360 | 1 | 1 | 1476-Induced draft fan speed changer | D2-Forced - Delayed | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3066 | 420 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 575 | 92 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.9999 | 360 | 1 | 1 | 1476-Induced draft fan speed changer | D2-Forced - Delayed | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OL | 800 | Miscellaneous | MRO | Off-Peak | 208.7227 | 4.64 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109 | 60 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.3 | 51 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5394.2 | 21 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32.0666 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.45 | 69 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149.6 | 44 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288.6 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 329.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 60 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 599.15 | 23 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 702 | 9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 887.0333 | 89 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1988.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2715.5333 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3097.7333 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4410 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30939.1665 | 271 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160 | 80 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14310 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 161.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 324 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 682.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 64394.5833 | 85 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 96.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.4251 | 110.33 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1186.1 | 409 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.7432 | 44.99 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.6666 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 495 | 36 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1150.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3362.5 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31241.6666 | 230 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.6 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154 | 154 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 292.8 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 622.8333 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 887.3333 | 44 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2088.0333 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2952.4666 | 134 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5156.2499 | 225 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8950 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11820.6664 | 340 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19410 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21880.5499 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230.433 | 446 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 255 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 645.8333 | 250 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1249.4167 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3477 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 809.8332 | 215 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 63.3333 | 95 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 194.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 828.0982 | 265.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 11391.555 | 365.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 397.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.0167 | 11 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.6333 | 7 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 214.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1392.0667 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6175 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22060 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 8.5833 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196 | 60 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 726.6664 | 400 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.4 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.9166 | 95 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 113.668 | 21.72 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.7999 | 126 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 242 | 110 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 713.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1470 | 245 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2487.8332 | 253 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.8 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.7 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.4166 | 119 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.3999 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196.1 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 319.5833 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 343.9333 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 500.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840.5 | 82 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1437 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5696.25 | 49 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19283.9999 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124900.6666 | 344 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.3332 | 280 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 536.6666 | 175 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 590.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1151.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3075 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4.5833 | 11 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 5425.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2142.0584 | 406.72 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3160.6665 | 220 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.106 | 66.46 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2129.5082 | 178.7 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 189.583 | 455 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.25 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.4166 | 127 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144.1 | 131 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 486 | 120 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1534.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2310.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2379 | 780 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3440.25 | 45 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6888.9331 | 616 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.1999 | 84 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.25 | 135 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.6666 | 260 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 178.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 211.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 268.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 422.8 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 507.6333 | 97 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 539.7333 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 761 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1875.2 | 64 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2365.1 | 134 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2423.5 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5543.3332 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22401 | 655 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.5 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1398.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2004.695 | 315.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4777.895 | 240.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1638 | 182 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 490.6666 | 230 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6969.9997 | 510 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2715.8428 | 178.87 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 169.9998 | 600 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.3333 | 110 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 541 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1232 | 616 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1419.3 | 54 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35153.3333 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.85 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.7 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 603 | 90 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 653.3333 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 842.8 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1210.4999 | 270 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4020.4999 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5116.8 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8696.5664 | 427 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 32.1667 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 480.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3345.3333 | 80 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 821.1 | 391 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 739.9998 | 600 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.75 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.0833 | 23 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.8333 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.6666 | 160 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 690.6666 | 80 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 895.1667 | 41 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2240.6 | 68 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5674.4998 | 270 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5746.2 | 314 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8884.1665 | 350 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9601.6666 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49041.4999 | 258 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21.9982 | 9.23 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.8333 | 235 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.1 | 69 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 290.4 | 44 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 373.9167 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 569.8 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1065.3 | 134 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1776.6666 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2364.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3835.6 | 344 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9115.9999 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.5 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.8333 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 187.6566 | 296.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 778.1666 | 203 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28674 | 360 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 55.0665 | 413 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 741.5975 | 2.17 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1202.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2727.183 | 533 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1014.9 | 102 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1316.9329 | 581 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16542.5 | 650 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2100.4498 | 603 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 221.3333 | 80 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2400 | 480 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3627.4999 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4653.6666 | 230 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8946.6666 | 160 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103170 | 190 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.5833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.1333 | 8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.6 | 44 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.7333 | 26 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116.1 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 297.5999 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 410 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 433.95 | 99 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 562.5 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 864.7833 | 89 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 869.5 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1001 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1157 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1831.6666 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2073.6 | 64 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2256.3333 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4999.9833 | 119 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160.8333 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2727.6666 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 38.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 11 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3230.66 | 16.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2074.9999 | 249 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 389.1667 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 567.3332 | 230 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 627.1999 | 84 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1958.6666 | 80 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20593.3333 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.0666 | 79 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.8499 | 129 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84 | 84 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 256.8 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 48 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 662.2 | 154 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1088 | 320 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1817.9333 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2318.1997 | 402 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2582.4 | 144 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5355.1333 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 148.5 | 55 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.8333 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.3333 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 368.5 | 134 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1075.5 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4157.3998 | 234 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 30.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 129 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 510.933 | 479 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1050.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22424.25 | 145 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 102.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 116.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9453 | 230 | 1 | 1 | 1480-Other induced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198.3333 | 175 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5884.9997 | 825 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 165.2665 | 268 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 4.515 | 30.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 188.5 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Other | BM | 800 | Miscellaneous | WECC | Winter | 27.4717 | 31.1 | 1 | 1 | 1480-Other induced draft fan problems | U2-Forced - Delayed | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 250.25 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 30.75 | 9 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 52.5 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 178.75 | 39 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 291.45 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 432.1 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 53.6667 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 136.5 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 9.1833 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 150.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 189.05 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 223.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 524.1666 | 34 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 23.3333 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 159.5 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 15 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 52.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 223.5667 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 75.8333 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 83.9167 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 247 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 131.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 186.8333 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1.6333 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 79 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 202.0667 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 219.9167 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4803.45 | 31 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1022 | 24 | 1 | 1 | 1487-Air heater (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 610.6666 | 160 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1401.6666 | 58 | 1 | 1 | 1487-Air heater (tubular) | U2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 467.6 | 28 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3652 | 44 | 1 | 1 | 1487-Air heater (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 425.9 | 6 | 1 | 1 | 1487-Air heater (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1440 | 6 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19358.9498 | 507 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1451.25 | 135 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 656.2666 | 107 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1078.8 | 124 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2068.3332 | 170 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2145 | 260 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3336.6667 | 44 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7355.5 | 313 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13025.6666 | 92 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15917 | 220 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 537.9 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 567 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 733.25 | 419 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1020 | 255 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1108.5832 | 265 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14699.8664 | 328 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1121 | 236 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2946.8998 | 342 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1080 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88470 | 360 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1269.8331 | 401 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14881.1372 | 260.92 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45561.0898 | 654.3 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26629 | 620 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34486.6664 | 400 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5695.433 | 539 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4957.3331 | 338 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6360 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 309.2582 | 218.3 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348 | 60 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1044.5833 | 115 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1831.8333 | 145 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1007 | 95 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 532 | 15.2 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 15 | 1 | 4 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1320 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 362.355 | 17.85 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21650.5498 | 747 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30857 | 523 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238 | 85 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20297.4999 | 345 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5665.65 | 107 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 17251.0862 | 642.1 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 736 | 64 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1940.8 | 48 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28450.95 | 401 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33198.9663 | 598 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.9333 | 62 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.4333 | 58 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 213.5416 | 102.5 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 435.0666 | 251 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 747 | 83 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 443 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1237.4999 | 270 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4348.6666 | 40 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 737.3332 | 316 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 859.1332 | 263 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2733.3333 | 100 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 650 | 260 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11843.9998 | 270 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 14030.0665 | 458 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23929.3994 | 876 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1331.6666 | 170 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2828.9999 | 180 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19987.5 | 195 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34534.3332 | 313 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.1667 | 25 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.5 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.25 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.7 | 91 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 712.25 | 185 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50 | 250 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.75 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5566 | 138 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.3333 | 116 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17468.3 | 307 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43582.1665 | 635 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1136629.9997 | 825 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 110337.8666 | 236 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18727.5 | 825 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 104985.8331 | 715 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1009.3333 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3900.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10738 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 216.0666 | 92.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 60 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1020.8999 | 147.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1477.6667 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77.7332 | 212 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2508.1665 | 298 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3178.3333 | 50 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3309.9332 | 262 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.66 | 4.37 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85.2498 | 465 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 25106.11 | 642.1 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12884.5 | 353 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 534.6665 | 401 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215.4167 | 47 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441 | 420 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 921.2499 | 165 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1800.5166 | 77 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8326.8265 | 390.32 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.3833 | 247 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.25 | 75 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.9999 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.6 | 138 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 138.0166 | 169 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 675.7664 | 418 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1978.5332 | 418 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40846.5 | 313 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 516.7333 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 605.7332 | 472 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 30 | 1 | 4 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 652 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357.5 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 30 | 1 | 25 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4501.1999 | 198 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 233694.6163 | 577 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66903 | 580 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 70846.25 | 785 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 40 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.75 | 45 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1440 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 65.75 | 52.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.9 | 94 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 131.88 | 12.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1053.6166 | 77 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1212.3453 | 243.28 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10901.6665 | 310 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1336 | 8 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330 | 30 | 1 | 2 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 660 | 55 | 1 | 18 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19017.9165 | 325 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 131693.3332 | 400 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1136.6667 | 44 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3422.6666 | 80 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4737.3333 | 80 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.9999 | 180 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 113.9666 | 52.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 285.5166 | 92.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 478.5 | 127.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 756.5 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2506.933 | 476 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.7999 | 138 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1091.9998 | 468 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1329.0664 | 448 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 540 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8735.9999 | 144 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4018 | 410 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27637.0832 | 475 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86739.55 | 523 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416217.3328 | 830 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66515.6665 | 620 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24570 | 360 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 53000.5332 | 256 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 475.3333 | 40 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4798 | 30 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490.8332 | 155 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11115.1666 | 85 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3832.4 | 78 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285.8333 | 50 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D2-Forced - Delayed | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165392.9998 | 270 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250 | 50 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 690 | 30 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1024.4667 | 22 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285 | 20 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D2-Forced - Delayed | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16432.5 | 75 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 659.75 | 7 | 1 | 1 | 1492-Air heater fouling (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 194.8333 | 10 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7448 | 35 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4291.5833 | 35 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2313.2266 | 35.2 | 1 | 1 | 1492-Air heater fouling (tubular) | U2-Forced - Delayed | 650-Fluidized Bed
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2018 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 2652.32 | 35.2 | 1 | 1 | 1492-Air heater fouling (tubular) | U2-Forced - Delayed | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55.428 | 8.94 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 50 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 491.3333 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 708.89 | 4.94 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2418.25 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3368.4 | 28.07 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4271.2333 | 97 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6581.25 | 75 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8616.12 | 136.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.2483 | 16.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.23 | 12.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.3333 | 8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.3 | 11 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.2 | 8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.16 | 18.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 157.5 | 14 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175 | 28 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.6667 | 44 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245 | 35 | 1 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276 | 23 | 1 | 3 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 315 | 21 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 540 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 875 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1540 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1700 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 1.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.75 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156.0785 | 5.41 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1287.5 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1299.6667 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2770.3693 | 23.08 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.6633 | 3.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.9998 | 492 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 292.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 458 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 576 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 774.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1800 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2033.5 | 147 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3412.75 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11158.56 | 22.14 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.25 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161 | 23 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172.0817 | 22.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 249.935 | 19.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288 | 24 | 1 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308 | 28 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 321.6 | 13.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 384 | 32 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 441.7667 | 29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 525 | 175 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 703 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1440 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.1333 | 22 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 419.2 | 64 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445.95 | 9.91 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 550 | 110 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2922.685 | 26.9 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 664.2 | 492 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3605.8833 | 193 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 19076 | 114 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.6667 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.1833 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1441.8333 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2208 | 23 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.8 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.75 | 20.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.0467 | 13.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.0417 | 20.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111 | 37 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.25 | 27 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 217.4999 | 90 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 348 | 29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 377.9167 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 455.535 | 57.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 510 | 170 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 528 | 22 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 684.61 | 22.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 845 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 856.615 | 21.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2583.02 | 12.98 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9672 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.4333 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 685.9999 | 168 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1993.7499 | 165 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4058.5333 | 122 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5031.25 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15133.4332 | 149 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21262.5 | 405 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115640.4163 | 577 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.9833 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.9 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216.2667 | 8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 391 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 422.0667 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2304 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6691.2 | 16.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7485.8333 | 65 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14240.16 | 19.14 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42 | 8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45 | 3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.75 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.5 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92 | 8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134.75 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 14 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296.0833 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 651 | 31 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 792 | 22 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1001 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21 | 21 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.965 | 6.9 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 819.21 | 14.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 830.3332 | 212 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1476 | 820 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5147.5 | 29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21486.6165 | 217 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226.8 | 2.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6389.9999 | 108 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640.2 | 194 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.6666 | 142 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 179.052 | 6.94 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222.6 | 18 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632.5667 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2400 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2803.206 | 13.02 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 9 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.215 | 18.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95.535 | 19.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102.29 | 19.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104.6666 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 262.5 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 273 | 39 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.5 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420 | 45 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 593.835 | 18.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1435.4165 | 265 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2304 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5503.513 | 12.66 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 584.8 | 102 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490.2083 | 12.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1035 | 34.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.1997 | 492 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.3998 | 492 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.8 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1152 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2721.7 | 17 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5546.2999 | 222 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26048.75 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.25 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.025 | 21.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 10 | 1 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.4 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.75 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176 | 22 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 22 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 213.3367 | 22.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 624 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1080 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1421.6883 | 23.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3049.8 | 13.26 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29424.3333 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.1 | 14.13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 207.87 | 5.07 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2018 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245.4666 | 28 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam